## Tab Index
S.No | Tab Index | Remarks
1 | Cable MTO Input | Input required from Client
2 | Tray MTO Input | Input required from Client
3 | Conduit MTO Input | Input required from Client
4 | Other Bulks MTO Input | Input required from Client
5 | HazClass Input | Input required from Client
6 | LF & Wage Rate Input | Preliminary input from Client - can be refined later as necessary
7 | Field Construction Plan | Preliminary input from Client - can be refined later as necessary
8 | Module Construction Plan | Preliminary input from Client - can be refined later as necessary
9 | Allowances | Output from EstiResource
20 | Output-Labor Detail | Output from EstiResource
11 | Output-Labor Summary Overview | Overviews, analysis and metrics from EstiResource
12 | Output-Quantities & Metrics | Overviews, analysis and metrics from EstiResource
13 | Labor Codes | EstiResource COA for information
Tabs Index - Click to navigate to desired tab

## Cable MTO Input
MTO_ID | WBS1 | WBS2/Area | WBS3/Sub-Area | WBS4 | WBS_L/Cable No. | Description | Units | Length | Tray_Cond_Buried | Mod__Field__Vendor | Installed By
610001 | Project A | Area1 | Sub Area 11 | Section 111 | B-10001 | 6c14awg Cu 600V TECK, Direct Buried | M | 58 | DirBuried | Field | Field Contract
610002 | Project A | Area1 | Sub Area 11 | Section 111 | C-10002 | 1pr16awg Shld 300V ACIC, Random Fill | M | 55 | Tray | Field | Field Contract
610003 | Project A | Area1 | Sub Area 11 | Section 111 | C-10003 | 1pr16awg Shld 300V ACIC, Random Fill | M | 55 | Tray | Field | Field Contract
610004 | Project A | Area1 | Sub Area 11 | Section 111 | C-10004 | 1pr16awg Shld 300V ACIC, Random Fill | M | 92 | Tray | Field | Field Contract
610005 | Project A | Area1 | Sub Area 11 | Section 111 | C-10005 | 1pr16awg Shld 300V ACIC, Random Fill | M | 92 | Tray | Field | Field Contract
610006 | Project A | Area1 | Sub Area 11 | Section 111 | C-10006 | 1pr16awg Shld 300V ACIC, Random Fill | M | 55 | Tray | Field | Field Contract
610007 | Project A | Area1 | Sub Area 11 | Section 111 | C-10007 | 1pr16awg Shld 300V ACIC, Random Fill | M | 55 | Tray | Field | Field Contract
610008 | Project A | Area1 | Sub Area 11 | Section 111 | C-10008 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610009 | Project A | Area1 | Sub Area 11 | Section 111 | C-10009 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610010 | Project A | Area1 | Sub Area 11 | Section 111 | C-10010 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610011 | Project A | Area1 | Sub Area 11 | Section 111 | C-10011 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610012 | Project A | Area1 | Sub Area 11 | Section 111 | C-10012 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610013 | Project A | Area1 | Sub Area 11 | Section 111 | C-10013 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610014 | Project A | Area1 | Sub Area 11 | Section 111 | C-10014 | 1pr16awg Shld 300V ACIC, Random Fill | M | 5 | Tray | Field | Field Contract
610015 | Project A | Area1 | Sub Area 11 | Section 111 | C-10015 | 1pr16awg Shld 300V ACIC, Random Fill | M | 5 | Tray | Field | Field Contract
610016 | Project A | Area1 | Sub Area 11 | Section 111 | C-10016 | 12pr16awg Shld 300V ACIC, Random Fill | M | 5 | Tray | Module | Module Contract
610017 | Project A | Area1 | Sub Area 11 | Section 111 | C-10017 | 20c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610018 | Project A | Area1 | Sub Area 11 | Section 111 | C-10018 | 12pr16awg Shld 300V ACIC, Random Fill | M | 5 | Tray | Module | Module Contract
610019 | Project A | Area1 | Sub Area 11 | Section 111 | C-10019 | 20c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610020 | Project A | Area1 | Sub Area 11 | Section 111 | CAT-10001 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610021 | Project A | Area1 | Sub Area 11 | Section 111 | C-10020 | 30c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Module | Module Contract
610022 | Project A | Area1 | Sub Area 11 | Section 111 | C-10021 | 4c14awg CU 600V TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610023 | Project A | Area1 | Sub Area 11 | Section 111 | C-10022 | 4c14awg CU 600V TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610024 | Project A | Area1 | Sub Area 11 | Section 111 | C-10023 | 4c14awg CU 600V TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610025 | Project A | Area1 | Sub Area 11 | Section 111 | C-10024 | 2pr16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610026 | Project A | Area1 | Sub Area 11 | Section 111 | C-10025 | 2pr16awg Shld 300V ACIC, Random Fill | M | 40 | Tray | Field | Field Contract
610027 | Project A | Area1 | Sub Area 11 | Section 111 | C-10026 | 2pr16awg Shld 300V ACIC, Random Fill | M | 90 | Tray | Field | Field Contract
610028 | Project A | Area1 | Sub Area 11 | Section 111 | C-10027 | 2pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610029 | Project A | Area1 | Sub Area 11 | Section 111 | C-10028 | 2pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610030 | Project A | Area1 | Sub Area 11 | Section 111 | C-10029 | 2pr16awg Shld 300V ACIC, Random Fill | M | 15 | Tray | Field | Field Contract
610031 | Project A | Area1 | Sub Area 11 | Section 111 | C-10030 | 2pr16awg Shld 300V ACIC, Random Fill | M | 15 | Tray | Field | Field Contract
610032 | Project A | Area1 | Sub Area 11 | Section 111 | C-10031 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610033 | Project A | Area1 | Sub Area 11 | Section 111 | C-10032 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610034 | Project A | Area1 | Sub Area 11 | Section 111 | C-10033 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610035 | Project A | Area1 | Sub Area 12 | Section 112 | C-10034 | 1triad16awg Shld 300V ACIC, Random Fill | M | 31 | Tray | Field | Field Contract
610036 | Project A | Area1 | Sub Area 12 | Section 112 | C-10035 | 1triad16awg Shld 300V ACIC, Random Fill | M | 55 | Tray | Field | Field Contract
610037 | Project A | Area1 | Sub Area 12 | Section 112 | C-10036 | 1triad16awg Shld 300V ACIC, Random Fill | M | 80 | Tray | Field | Field Contract
610038 | Project A | Area1 | Sub Area 12 | Section 112 | C-10037 | 1triad16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610039 | Project A | Area1 | Sub Area 12 | Section 112 | C-10038 | 1triad16awg Shld 300V ACIC, Random Fill | M | 15 | Tray | Field | Field Contract
610040 | Project A | Area1 | Sub Area 12 | Section 112 | C-10039 | 1c14awg Cu, Random Fill | M | 5 | Tray | Module | Module Contract
610041 | Project A | Area1 | Sub Area 12 | Section 112 | P-10003 | 2c1/0awg Cu 1kV TECK | M | 5 | Tray | Module | Module Contract
610042 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10001 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610043 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10002 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610044 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10003 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610045 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10004 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610046 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10005 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610047 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10006 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610048 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10007 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610049 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10008 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610050 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10009 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610051 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10010 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610052 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10011 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610053 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10012 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610054 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10013 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610055 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10014 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610056 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10015 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610057 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10016 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610058 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10017 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610059 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10018 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610060 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10019 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610061 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10020 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610062 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10021 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610063 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10022 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610064 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10023 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610065 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10024 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610066 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10025 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610067 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10026 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610068 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10027 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610069 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10028 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610070 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10029 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610071 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10030 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610072 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10031 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610073 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10032 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610074 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10033 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610075 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10034 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610076 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10035 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610077 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10036 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610078 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10037 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610079 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10038 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610080 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10039 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610081 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10040 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610082 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10041 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610083 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10042 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610084 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10043 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610085 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10044 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610086 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10045 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610087 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10046 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610088 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10047 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610089 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10048 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610090 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10049 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610091 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10050 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610092 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10051 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610093 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10052 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610094 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10053 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610095 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10054 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610096 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10055 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610097 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10056 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610098 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10057 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610099 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10058 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610100 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10059 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610101 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10060 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610102 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10061 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610103 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10062 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610104 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10063 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610105 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10064 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610106 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10065 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610107 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10066 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610108 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10067 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610109 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10068 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610110 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10069 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610111 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10070 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610112 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10071 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610113 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10072 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610114 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10073 | 3c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610115 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10074 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610116 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10075 | 2c16awg OS+TC 300V FEP, CMP, Random Fill | M | 15 | Cond | Module | Module Contract
610117 | Project A | Area1 | Sub Area 12 | Section 112 | FO-10001 | Fiber-Optic 24 x SM, Armoured & Jacketed, Random Fill | M | 333 | Tray | Field | Field Contract
610118 | Project A | Area1 | Sub Area 12 | Section 112 | C-10106 | 20c14awg Cu 600V TECK, Random Fill | M | 61 | Tray | Field | Field Contract
610119 | Project A | Area1 | Sub Area 12 | Section 112 | C-10107 | 20c14awg Cu 600V TECK, Random Fill | M | 61 | Tray | Field | Field Contract
610120 | Project A | Area1 | Sub Area 12 | Section 112 | C-10108 | 20c14awg Cu 600V TECK, Random Fill | M | 61 | Tray | Field | Field Contract
610121 | Project A | Area1 | Sub Area 12 | Section 112 | C-10109 | 20c14awg Cu 600V TECK, Random Fill | M | 61 | Tray | Field | Field Contract
610122 | Project A | Area1 | Sub Area 12 | Section 112 | C-10110 | 20c14awg Cu 600V TECK, Random Fill | M | 61 | Tray | Field | Field Contract
610123 | Project A | Area2 | Sub Area 21 | Section 211 | C-10111 | 8pr16awg Shld 300V ACIC, Random Fill | M | 61 | Tray | Field | Field Contract
610124 | Project A | Area2 | Sub Area 21 | Section 211 | C-10112 | 8pr16awg Shld 300V ACIC, Random Fill | M | 61 | Tray | Field | Field Contract
610125 | Project A | Area2 | Sub Area 21 | Section 211 | C-10113 | 4pr16awg Shld 300V ACIC, Random Fill | M | 61 | Tray | Field | Field Contract
610126 | Project A | Area2 | Sub Area 21 | Section 211 | C-10114 | 8triad 16awg 300V ACIC, Random Fill | M | 61 | Tray | Field | Field Contract
610127 | Project A | Area2 | Sub Area 21 | Section 211 | C-10115 | 4pr16awg Shld 300V ACIC, Random Fill | M | 241 | Tray | Field | Field Contract
610128 | Project A | Area2 | Sub Area 21 | Section 211 | C-10116 | 4c14awg CU 600V TECK, Random Fill | M | 100 | Tray | Field | Field Contract
610129 | Project A | Area2 | Sub Area 21 | Section 211 | P-10004 | 2c6awg Cu 1kV TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610130 | Project A | Area2 | Sub Area 21 | Section 211 | C-10117 | 6c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610131 | Project A | Area2 | Sub Area 21 | Section 211 | C-10118 | 6c14awg Cu 600V TECK, Random Fill | M | 47 | Tray | Field | Field Contract
610132 | Project A | Area2 | Sub Area 21 | Section 211 | C-10119 | 30c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610133 | Project A | Area2 | Sub Area 21 | Section 211 | C-10120 | 30c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610134 | Project A | Area2 | Sub Area 21 | Section 211 | C-10121 | 30c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610135 | Project A | Area2 | Sub Area 21 | Section 211 | C-10122 | 30c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610136 | Project A | Area2 | Sub Area 21 | Section 211 | C-10123 | 8pr16awg Shld 300V ACIC, Random Fill | M | 76 | Tray | Field | Field Contract
610137 | Project A | Area2 | Sub Area 21 | Section 211 | C-10124 | 8pr16awg Shld 300V ACIC, Random Fill | M | 76 | Tray | Field | Field Contract
610138 | Project A | Area2 | Sub Area 21 | Section 211 | C-10125 | 4c14awg CU 600V TECK, Random Fill | M | 18 | Tray | Field | Field Contract
610139 | Project A | Area2 | Sub Area 21 | Section 211 | C-10126 | 4c14awg CU 600V TECK, Random Fill | M | 13 | Tray | Field | Field Contract
610140 | Project A | Area2 | Sub Area 21 | Section 211 | C-10127 | 4pr16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610141 | Project A | Area2 | Sub Area 21 | Section 211 | C-10128 | 2pr16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610142 | Project A | Area2 | Sub Area 21 | Section 211 | C-10129 | 4pr16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610143 | Project A | Area2 | Sub Area 21 | Section 211 | C-10130 | 2pr16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610144 | Project A | Area2 | Sub Area 21 | Section 211 | C-10131 | 4pr16awg Shld 300V ACIC, Random Fill | M | 32 | Tray | Field | Field Contract
610145 | Project A | Area2 | Sub Area 21 | Section 211 | C-10132 | 2pr16awg Shld 300V ACIC, Random Fill | M | 32 | Tray | Field | Field Contract
610146 | Project A | Area2 | Sub Area 21 | Section 211 | C-10133 | 4pr16awg Shld 300V ACIC, Random Fill | M | 32 | Tray | Field | Field Contract
610147 | Project A | Area2 | Sub Area 21 | Section 211 | C-10134 | 2pr16awg Shld 300V ACIC, Random Fill | M | 32 | Tray | Field | Field Contract
610148 | Project A | Area2 | Sub Area 21 | Section 211 | P-10005 | 20c10awg Cu 600V CONDUIT, Random Fill | M | 10 | Tray | Field | Field Contract
610149 | Project A | Area2 | Sub Area 21 | Section 211 | C-10135 | 4c14awg CU 600V TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610150 | Project A | Area2 | Sub Area 21 | Section 211 | C-10136 | 4c14awg CU 600V TECK, Random Fill | M | 35 | Tray | Field | Field Contract
610151 | Project A | Area2 | Sub Area 21 | Section 211 | C-10137 | 4c14awg CU 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610152 | Project A | Area2 | Sub Area 21 | Section 211 | C-10138 | 4c14awg CU 600V TECK, Random Fill | M | 120 | Tray | Field | Field Contract
610153 | Project A | Area2 | Sub Area 21 | Section 211 | C-10139 | 4c14awg CU 600V TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610154 | Project A | Area2 | Sub Area 21 | Section 211 | C-10140 | 4c14awg CU 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610155 | Project A | Area2 | Sub Area 21 | Section 211 | C-10141 | 4c14awg CU 600V TECK, Random Fill | M | 70 | Tray | Field | Field Contract
610156 | Project A | Area2 | Sub Area 21 | Section 211 | C-10142 | 4c14awg CU 600V TECK, Random Fill | M | 65 | Tray | Field | Field Contract
610157 | Project A | Area2 | Sub Area 21 | Section 211 | P-10006 | 2c10awg Cu 600V TECK, Random Fill | M | 30 | Tray | Field | Field Contract
610158 | Project A | Area2 | Sub Area 21 | Section 211 | C-10143 | 10c14awg Cu 600V TECK, Random Fill | M | 92 | Tray | Field | Field Contract
610159 | Project A | Area2 | Sub Area 21 | Section 211 | P-10007 | 2c10awg Cu 600V TECK, Random Fill | M | 40 | Tray | Field | Field Contract
610160 | Project A | Area2 | Sub Area 21 | Section 211 | C-10144 | 10c14awg Cu 600V TECK, Random Fill | M | 126 | Tray | Field | Field Contract
610161 | Project A | Area2 | Sub Area 21 | Section 211 | P-10008 | 2c10awg Cu 600V TECK, Random Fill | M | 55 | Tray | Field | Field Contract
610162 | Project A | Area2 | Sub Area 21 | Section 211 | C-10145 | 10c14awg Cu 600V TECK, Random Fill | M | 143 | Tray | Field | Field Contract
610163 | Project A | Area2 | Sub Area 21 | Section 211 | C-10146 | 6c14awg Cu 600V TECK, Random Fill | M | 30 | Tray | Field | Field Contract
610164 | Project A | Area2 | Sub Area 21 | Section 211 | C-10147 | 6c14awg Cu 600V TECK, Random Fill | M | 13 | Tray | Field | Field Contract
610165 | Project A | Area2 | Sub Area 21 | Section 211 | C-10148 | 6c14awg Cu 600V TECK, Random Fill | M | 30 | Tray | Field | Field Contract
610166 | Project A | Area2 | Sub Area 21 | Section 211 | C-10149 | 6c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610167 | Project A | Area2 | Sub Area 21 | Section 211 | P-10009 | 2c10awg Cu 600V TECK, Random Fill | M | 40 | Tray | Field | Field Contract
610168 | Project A | Area2 | Sub Area 21 | Section 211 | P-10010 | 2c10awg Cu 600V TECK, Random Fill | M | 40 | Tray | Field | Field Contract
610169 | Project A | Area2 | Sub Area 21 | Section 211 | P-10011 | 2c10awg Cu 600V TECK, Random Fill | M | 23 | Tray | Field | Field Contract
610170 | Project A | Area2 | Sub Area 21 | Section 211 | P-10012 | 2c10awg Cu 600V TECK, Random Fill | M | 60 | Tray | Field | Field Contract
610171 | Project A | Area2 | Sub Area 21 | Section 211 | P-10013 | 2c8awg Cu 1kV TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610172 | Project A | Area2 | Sub Area 21 | Section 211 | P-10014 | 2c8awg Cu 1kV TECK, Random Fill | M | 181 | Tray | Field | Field Contract
610173 | Project A | Area2 | Sub Area 21 | Section 211 | P-10015 | 2c10awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610174 | Project A | Area2 | Sub Area 21 | Section 211 | P-10016 | 2c10awg Cu 600V TECK, Random Fill | M | 195 | Tray | Field | Field Contract
610175 | Project A | Area2 | Sub Area 21 | Section 211 | C-10150 | 10c14awg Cu 600V TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610176 | Project A | Area2 | Sub Area 21 | Section 211 | P-10017 | 30c10awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610177 | Project A | Area2 | Sub Area 21 | Section 211 | C-10151 | 6c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610178 | Project A | Area2 | Sub Area 21 | Section 211 | C-10152 | 6c14awg Cu 600V TECK, Random Fill | M | 17 | Tray | Module | Module Contract
610179 | Project A | Area2 | Sub Area 21 | Section 211 | C-10153 | 6c14awg Cu 600V TECK, Random Fill | M | 17 | Tray | Module | Module Contract
610180 | Project A | Area2 | Sub Area 21 | Section 211 | C-10154 | 6c14awg Cu 600V TECK, Random Fill | M | 11 | Tray | Module | Module Contract
610181 | Project A | Area2 | Sub Area 21 | Section 211 | C-10155 | 8pr14awg Shld 300v ACIC, Random Fill | M | 241 | Tray | Field | Field Contract
610182 | Project A | Area2 | Sub Area 21 | Section 211 | C-10156 | 8pr16awg Shld 300V ACIC, Random Fill | M | 241 | Tray | Field | Field Contract
610183 | Project A | Area2 | Sub Area 21 | Section 211 | C-10157 | 20c14awg Cu 600V TECK, Random Fill | M | 45 | Tray | Field | Field Contract
610184 | Project A | Area2 | Sub Area 21 | Section 211 | C-10158 | 6pr16awg Shld 300V ACIC, Random Fill | M | 45 | Tray | Field | Field Contract
610185 | Project A | Area2 | Sub Area 21 | Section 211 | P-10018 | 2c10awg Cu 600V TECK, Random Fill | M | 132 | Tray | Field | Field Contract
610186 | Project A | Area2 | Sub Area 21 | Section 211 | P-10019 | 3c12awg | M | 5 | Tray | Field | Field Contract
610187 | Project A | Area2 | Sub Area 21 | Section 211 | P-10020 | 4c6awg | M | 316 | Tray | Field | Field Contract
610188 | Project A | Area2 | Sub Area 21 | Section 211 | P-10021 | 2c10awg | M | 207 | Tray | Field | Field Contract
610189 | Project A | Area2 | Sub Area 21 | Section 211 | P-10022 | 2c10awg | M | 195 | Tray | Field | Field Contract
610190 | Project A | Area2 | Sub Area 21 | Section 211 | P-10023 | 4c6awg | M | 316 | Tray | Field | Field Contract
610191 | Project A | Area2 | Sub Area 21 | Section 211 | P-10024 | 4c6awg | M | 149 | Tray | Field | Field Contract
610192 | Project A | Area2 | Sub Area 21 | Section 211 | P-10025 | 2c10awg | M | 67 | Tray | Field | Field Contract
610193 | Project A | Area2 | Sub Area 21 | Section 211 | P-10026 | 2c10awg | M | 67 | Tray | Field | Field Contract
610194 | Project A | Area2 | Sub Area 21 | Section 211 | P-10027 | 2c10awg | M | 60 | Tray | Field | Field Contract
610195 | Project A | Area2 | Sub Area 21 | Section 211 | P-10028 | 2c12awg | M | 5 | Tray | Module | Module Contract
610196 | Project A | Area2 | Sub Area 21 | Section 211 | P-10029 | 2c10awg | M | 161 | Tray | Field | Field Contract
610197 | Project A | Area2 | Sub Area 21 | Section 211 | P-10030 | 2c10awg | M | 50 | Tray | Field | Field Contract
610198 | Project A | Area2 | Sub Area 21 | Section 211 | P-10031 | 2c10awg | M | 45 | Tray | Field | Field Contract
610199 | Project A | Area2 | Sub Area 21 | Section 211 | P-10032 | 3c12awg | M | 15 | Tray | Module | Module Contract
610200 | Project A | Area2 | Sub Area 21 | Section 211 | P-10033 | 2c10awg | M | 195 | Tray | Field | Field Contract
610201 | Project A | Area2 | Sub Area 21 | Section 211 | C-10159 | 1pr16awg, Unarmored | M | 11 | Tray | Field | Field Contract
610202 | Project A | Area2 | Sub Area 21 | Section 211 | C-10160 | 1pr16awg, Unarmored | M | 13 | Tray | Field | Field Contract
610203 | Project A | Area2 | Sub Area 21 | Section 211 | P-10034 | 6c10awg | M | 5 | Tray | Field | Field Contract
610204 | Project A | Area2 | Sub Area 21 | Section 211 | P-10035 | 2c10awg | M | 132 | Tray | Field | Field Contract
610205 | Project A | Area2 | Sub Area 21 | Section 211 | P-10036 | 30c10awg | M | 60 | Tray | Field | Field Contract
610206 | Project A | Area2 | Sub Area 21 | Section 211 | P-10037 | 2c12awg | M | 10 | Tray | Module | Module Contract
610207 | Project A | Area2 | Sub Area 21 | Section 211 | P-10038 | 2c12awg | M | 10 | Tray | Module | Module Contract
610208 | Project A | Area2 | Sub Area 21 | Section 211 | P-10039 | 2c12awg | M | 5 | Tray | Module | Module Contract
610209 | Project A | Area2 | Sub Area 21 | Section 211 | P-10040 | 2c12awg | M | 24 | Tray | Module | Module Contract
610210 | Project A | Area2 | Sub Area 21 | Section 211 | P-10041 | 2c12awg | M | 10 | Tray | Module | Module Contract
610211 | Project A | Area2 | Sub Area 21 | Section 211 | P-10042 | 2c12awg | M | 10 | Tray | Module | Module Contract
610212 | Project A | Area2 | Sub Area 21 | Section 211 | P-10043 | 2c12awg | M | 14 | Tray | Module | Module Contract
610213 | Project A | Area2 | Sub Area 21 | Section 211 | P-10044 | 2c12awg | M | 10 | Tray | Module | Module Contract
610214 | Project A | Area2 | Sub Area 21 | Section 211 | P-10045 | 2c12awg | M | 5 | Tray | Module | Module Contract
610215 | Project A | Area2 | Sub Area 21 | Section 211 | P-10046 | 20c10awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610216 | Project A | Area2 | Sub Area 21 | Section 211 | P-10047 | 2c10awg Cu 600V TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610217 | Project A | Area2 | Sub Area 21 | Section 211 | P-10048 | 2c2awg Cu 1kV TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610218 | Project A | Area2 | Sub Area 21 | Section 211 | P-10049 | 6c10awg Cu 600V TECK, Random Fill | M | 18 | Tray | Module | Module Contract
610219 | Project A | Area2 | Sub Area 21 | Section 211 | P-10050 | 6c10awg Cu 600V TECK, Random Fill | M | 20 | Tray | Module | Module Contract
610220 | Project A | Area2 | Sub Area 21 | Section 211 | P-10051 | 6c10awg Cu 600V TECK, Random Fill | M | 22 | Tray | Module | Module Contract
610221 | Project A | Area2 | Sub Area 21 | Section 211 | C-10161 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610222 | Project A | Area2 | Sub Area 21 | Section 211 | C-10162 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610223 | Project A | Area2 | Sub Area 21 | Section 211 | C-10163 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610224 | Project A | Area2 | Sub Area 21 | Section 211 | C-10164 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610225 | Project A | Area2 | Sub Area 21 | Section 211 | C-10165 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610226 | Project A | Area2 | Sub Area 21 | Section 211 | C-10166 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610227 | Project A | Area2 | Sub Area 21 | Section 211 | C-10167 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610228 | Project A | Area2 | Sub Area 21 | Section 211 | C-10168 | 4c14awg CU 600V TECK, Random Fill | M | 18 | Tray | Field | Field Contract
610229 | Project A | Area2 | Sub Area 21 | Section 211 | C-10169 | 4c14awg CU 600V TECK, Random Fill | M | 13 | Tray | Field | Field Contract
610230 | Project A | Area2 | Sub Area 21 | Section 211 | C-10170 | 4c14awg CU 600V TECK, Random Fill | M | 14 | Tray | Field | Field Contract
610231 | Project A | Area2 | Sub Area 21 | Section 211 | C-10171 | 40c14awg Cu 600V TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610232 | Project A | Area2 | Sub Area 21 | Section 211 | B-10002 | 3c4/0awg Cu 1kV TECK, Direct Buried | M | 20 | DirBuried | Field | Field Contract
610233 | Project A | Area2 | Sub Area 21 | Section 211 | B-10003 | 3c4/0awg Cu 1kV TECK, Direct Buried | M | 20 | DirBuried | Field | Field Contract
610234 | Project A | Area2 | Sub Area 21 | Section 211 | B-10004 | 3c4/0awg Cu 1kV TECK, Direct Buried | M | 20 | DirBuried | Field | Field Contract
610235 | Project A | Area2 | Sub Area 21 | Section 211 | B-10005 | 3c4/0awg Cu 1kV TECK, Direct Buried | M | 20 | DirBuried | Field | Field Contract
610236 | Project A | Area2 | Sub Area 21 | Section 211 | P-10056 | 2c10awg Cu 600V TECK, Random Fill | M | 50 | Tray | Field | Field Contract
610237 | Project A | Area2 | Sub Area 22 | Section 221 | C-10172 | 8triad 16awg, Unarmored | M | 50 | Tray | Field | Field Contract
610238 | Project A | Area2 | Sub Area 22 | Section 221 | P-10057 | 3c500mcm | M | 50 | Tray | Field | Field Contract
610239 | Project A | Area2 | Sub Area 22 | Section 221 | P-10058 | 2c10awg | M | 60 | Tray | Field | Field Contract
610240 | Project A | Area2 | Sub Area 22 | Section 221 | C-10173 | 8triad 16awg 300V ACIC, Random Fill | M | 60 | Tray | Field | Field Contract
610241 | Project A | Area2 | Sub Area 22 | Section 221 | P-10059 | 3c500mcm | M | 60 | Tray | Field | Field Contract
610242 | Project A | Area2 | Sub Area 22 | Section 221 | C-10174 | 10c14awg | M | 50 | Tray | Field | Field Contract
610243 | Project A | Area2 | Sub Area 22 | Section 221 | C-10175 | 10c14awg | M | 60 | Tray | Field | Field Contract
610244 | Project A | Area2 | Sub Area 22 | Section 221 | C-10176 | 12c14awg | M | 316 | Tray | Field | Field Contract
610245 | Project A | Area2 | Sub Area 22 | Section 221 | P-10060 | 3c12awg | M | 209 | Tray | Field | Field Contract
610246 | Project A | Area2 | Sub Area 22 | Section 221 | P-10061 | 3c12awg | M | 207 | Tray | Field | Field Contract
610247 | Project A | Area2 | Sub Area 22 | Section 221 | P-10062 | 3c12awg | M | 205 | Tray | Field | Field Contract
610248 | Project A | Area2 | Sub Area 22 | Section 221 | P-10063 | 3c12awg | M | 120 | Tray | Field | Field Contract
610249 | Project A | Area2 | Sub Area 22 | Section 221 | P-10064 | 3c12awg | M | 100 | Tray | Field | Field Contract
610250 | Project A | Area2 | Sub Area 22 | Section 221 | P-10065 | 3c12awg | M | 120 | Tray | Field | Field Contract
610251 | Project A | Area2 | Sub Area 22 | Section 221 | P-10066 | 3c12awg | M | 100 | Tray | Field | Field Contract
610252 | Project A | Area2 | Sub Area 22 | Section 221 | P-10067 | 3c12awg | M | 126 | Tray | Field | Field Contract
610253 | Project A | Area2 | Sub Area 22 | Section 221 | P-10068 | 3c12awg | M | 204 | Tray | Field | Field Contract
610254 | Project A | Area2 | Sub Area 22 | Section 221 | P-10069 | 3c12awg | M | 207 | Tray | Field | Field Contract
610255 | Project A | Area2 | Sub Area 22 | Section 221 | P-10070 | 3c12awg Cu 600V TECK, Random Fill | M | 60 | Tray | Field | Field Contract
610256 | Project A | Area2 | Sub Area 22 | Section 221 | P-10071 | 3c12awg | M | 55 | Tray | Field | Field Contract
610257 | Project A | Area2 | Sub Area 22 | Section 221 | P-10072 | 3c12awg | M | 189 | Tray | Field | Field Contract
610258 | Project A | Area2 | Sub Area 22 | Section 221 | P-10073 | 3c12awg | M | 195 | Tray | Field | Field Contract
610259 | Project A | Area2 | Sub Area 22 | Section 221 | P-10074 | 3c12awg | M | 132 | Tray | Field | Field Contract
610260 | Project A | Area2 | Sub Area 22 | Section 221 | P-10075 | 3c12awg | M | 126 | Tray | Field | Field Contract
610261 | Project A | Area2 | Sub Area 22 | Section 221 | P-10076 | 3c12awg | M | 132 | Tray | Field | Field Contract
610262 | Project A | Area2 | Sub Area 22 | Section 221 | P-10077 | 3c12awg | M | 126 | Tray | Field | Field Contract
610263 | Project A | Area2 | Sub Area 22 | Section 221 | P-10078 | 3c12awg | M | 138 | Tray | Field | Field Contract
610264 | Project A | Area2 | Sub Area 22 | Section 221 | P-10079 | 3c12awg | M | 316 | Tray | Field | Field Contract
610265 | Project A | Area2 | Sub Area 22 | Section 221 | C-10177 | 20c14awg | M | 25 | Tray | Field | Field Contract
610266 | Project A | Area2 | Sub Area 22 | Section 221 | P-10080 | 3c8awg | M | 316 | Tray | Field | Field Contract
610267 | Project A | Area2 | Sub Area 22 | Section 221 | P-10081 | 3c1awg | M | 15 | Tray | Field | Field Contract
610268 | Project A | Area2 | Sub Area 22 | Section 221 | P-10082 | 3c500mcm TECK | M | 20 | Tray | Module | Module Contract
610269 | Project A | Area2 | Sub Area 22 | Section 221 | P-10083 | 3c500mcm | M | 23 | Tray | Module | Module Contract
610270 | Project A | Area2 | Sub Area 22 | Section 221 | P-10084 | 3c500mcm | M | 23 | Tray | Module | Module Contract
610271 | Project A | Area2 | Sub Area 22 | Section 221 | P-10085 | 3c2awg | M | 22 | Tray | Module | Module Contract
610272 | Project A | Area2 | Sub Area 22 | Section 221 | P-10086 | 3c2awg | M | 22 | Tray | Module | Module Contract
610273 | Project A | Area2 | Sub Area 22 | Section 221 | P-10087 | 3c6awg Cu 1kV TECK, Random Fill | M | 60 | Tray | Field | Field Contract
610274 | Project A | Area2 | Sub Area 22 | Section 221 | P-10088 | 3c6awg Cu 1kV TECK, Random Fill | M | 75 | Tray | Field | Field Contract
610275 | Project A | Area2 | Sub Area 22 | Section 221 | P-10089 | 3c6awg Cu 1kV TECK, Random Fill | M | 75 | Tray | Field | Field Contract
610276 | Project A | Area2 | Sub Area 22 | Section 221 | P-10090 | 3c6awg Cu 1kV TECK, Random Fill | M | 85 | Tray | Field | Field Contract
610277 | Project A | Area2 | Sub Area 22 | Section 221 | P-10091 | 3c6awg Cu 1kV TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610278 | Project A | Area2 | Sub Area 22 | Section 221 | P-10092 | 3c6awg Cu 1kV TECK, Random Fill | M | 126 | Tray | Field | Field Contract
610279 | Project A | Area2 | Sub Area 22 | Section 221 | P-10093 | 3c6awg Cu 1kV TECK, Random Fill | M | 126 | Tray | Field | Field Contract
610280 | Project A | Area2 | Sub Area 22 | Section 221 | P-10094 | 3c6awg Cu 1kV TECK, Random Fill | M | 143 | Tray | Field | Field Contract
610281 | Project A | Area2 | Sub Area 22 | Section 221 | P-10095 | 3c8awg Cu 1kV TECK, Random Fill | M | 20 | Tray | Module | Module Contract
610282 | Project A | Area2 | Sub Area 22 | Section 221 | P-10096 | 3c8awg Cu 1kV TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610283 | Project A | Area2 | Sub Area 22 | Section 221 | P-10097 | 3c8awg Cu 1kV TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610284 | Project A | Area2 | Sub Area 22 | Section 221 | P-10098 | 3c8awg Cu 1kV TECK, Random Fill | M | 18 | Tray | Module | Module Contract
610285 | Project A | Area2 | Sub Area 22 | Section 221 | CAT-10002 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 15 | Tray | Module | Module Contract
610286 | Project A | Area2 | Sub Area 22 | Section 221 | C-10178 | 12c14awg Cu 600V TECK, Random Fill | M | 30 | Tray | Field | Field Contract
610287 | Project A | Area2 | Sub Area 22 | Section 221 | P-10100 | 3c8awg Cu 1kV TECK, Random Fill | M | 20 | Tray | Module | Module Contract
610288 | Project A | Area2 | Sub Area 22 | Section 221 | P-10101 | 3c8awg Cu 1kV TECK, Random Fill | M | 12 | Tray | Module | Module Contract
610289 | Project A | Area2 | Sub Area 22 | Section 221 | P-10102 | 3c8awg Cu 1kV TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610290 | Project A | Area2 | Sub Area 22 | Section 221 | P-10103 | 3c8awg Cu 1kV TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610291 | Project A | Area2 | Sub Area 22 | Section 221 | P-10104 | 3c10awg Cu 600V TECK, Random Fill | M | 100 | Tray | Field | Field Contract
610292 | Project A | Area2 | Sub Area 22 | Section 221 | P-10105 | 3c10awg Cu 600V TECK, Random Fill | M | 124 | Tray | Field | Field Contract
610293 | Project A | Area2 | Sub Area 22 | Section 221 | P-10106 | 3c10awg Cu 600V TECK, Random Fill | M | 128 | Tray | Field | Field Contract
610294 | Project A | Area2 | Sub Area 22 | Section 221 | P-10107 | 3c10awg Cu 600V TECK, Random Fill | M | 138 | Tray | Field | Field Contract
610295 | Project A | Area2 | Sub Area 22 | Section 221 | P-10108 | 3c10awg Cu 600V TECK, Random Fill | M | 142 | Tray | Field | Field Contract
610296 | Project A | Area2 | Sub Area 22 | Section 221 | P-10109 | 3c10awg Cu 600V TECK, Random Fill | M | 151 | Tray | Field | Field Contract
610297 | Project A | Area2 | Sub Area 22 | Section 221 | P-10110 | 3c12awg Cu 600V TECK, Random Fill | M | 43 | Tray | Field | Field Contract
610298 | Project A | Area2 | Sub Area 22 | Section 221 | C-10179 | 20c14awg Cu 600V TECK, Random Fill | M | 65 | Tray | Field | Field Contract
610299 | Project A | Area2 | Sub Area 22 | Section 221 | C-10180 | 20c14awg Cu 600V TECK, Random Fill | M | 65 | Tray | Field | Field Contract
610300 | Project A | Area2 | Sub Area 22 | Section 221 | C-10181 | 30c14awg Cu 600V TECK, Random Fill | M | 20 | Tray | Module | Module Contract
610301 | Project A | Area2 | Sub Area 22 | Section 221 | C-10182 | 30c14awg Cu 600V TECK, Random Fill | M | 20 | Tray | Module | Module Contract
610302 | Project A | Area2 | Sub Area 22 | Section 221 | C-10183 | 30c14awg Cu 600V TECK, Random Fill | M | 20 | Tray | Module | Module Contract
610303 | Project A | Area2 | Sub Area 22 | Section 221 | P-10111 | 3c8awg Cu 1kV TECK, Random Fill | M | 30 | Tray | Field | Field Contract
610304 | Project A | Area2 | Sub Area 22 | Section 221 | P-10112 | 3c4/0awg Cu 1kV TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610305 | Project A | Area2 | Sub Area 22 | Section 221 | P-10113 | 3c4/0awg Cu 1kV TECK, Random Fill | M | 18 | Tray | Module | Module Contract
610306 | Project A | Area2 | Sub Area 22 | Section 221 | P-10114 | 3c8awg Cu 1kV TECK, Random Fill | M | 14 | Tray | Module | Module Contract
610307 | Project A | Area2 | Sub Area 22 | Section 221 | P-10115 | 3c12awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610308 | Project A | Area2 | Sub Area 22 | Section 221 | P-10116 | 3c1awg Cu 1kV TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610309 | Project A | Area2 | Sub Area 22 | Section 221 | P-10117 | 3c12awg Cu 600V TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610310 | Project A | Area2 | Sub Area 22 | Section 221 | P-10118 | 3c1awg Cu 1kV TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610311 | Project A | Area2 | Sub Area 22 | Section 221 | P-10119 | 3c12awg Cu 600V TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610312 | Project A | Area2 | Sub Area 22 | Section 221 | P-10120 | 3c1awg Cu 1kV TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610313 | Project A | Area2 | Sub Area 22 | Section 221 | P-10121 | 3c12awg Cu 600V TECK, Random Fill | M | 65 | Tray | Field | Field Contract
610314 | Project A | Area2 | Sub Area 22 | Section 221 | P-10122 | 3c12awg Cu 600V TECK, Random Fill | M | 90 | Tray | Field | Field Contract
610315 | Project A | Area2 | Sub Area 22 | Section 221 | P-10123 | 3c12awg Cu 600V TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610316 | Project A | Area2 | Sub Area 22 | Section 221 | P-10124 | 3c12awg Cu 600V TECK, Random Fill | M | 120 | Tray | Field | Field Contract
610317 | Project A | Area2 | Sub Area 22 | Section 221 | P-10125 | 3c12awg Cu 600V TECK, Random Fill | M | 126 | Tray | Field | Field Contract
610318 | Project A | Area2 | Sub Area 22 | Section 221 | P-10126 | 3c12awg Cu 600V TECK, Random Fill | M | 138 | Tray | Field | Field Contract
610319 | Project A | Area3 | Sub Area 31 | Section 311 | C-10184 | 12c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610320 | Project A | Area3 | Sub Area 31 | Section 311 | C-10185 | 12c14awg Cu 600V TECK, Random Fill | M | 34 | Tray | Field | Field Contract
610321 | Project A | Area3 | Sub Area 31 | Section 311 | C-10186 | 12c14awg Cu 600V TECK, Random Fill | M | 28 | Tray | Field | Field Contract
610322 | Project A | Area3 | Sub Area 31 | Section 311 | C-10187 | 12c14awg Cu 600V TECK, Random Fill | M | 34 | Tray | Field | Field Contract
610323 | Project A | Area3 | Sub Area 31 | Section 311 | C-10188 | 12c14awg Cu 600V TECK, Random Fill | M | 33 | Tray | Field | Field Contract
610324 | Project A | Area3 | Sub Area 31 | Section 311 | C-10189 | 12c14awg Cu 600V TECK, Random Fill | M | 33 | Tray | Field | Field Contract
610325 | Project A | Area3 | Sub Area 31 | Section 311 | C-10190 | 12c14awg Cu 600V TECK, Random Fill | M | 33 | Tray | Field | Field Contract
610326 | Project A | Area3 | Sub Area 31 | Section 311 | C-10191 | 12c14awg Cu 600V TECK, Random Fill | M | 33 | Tray | Field | Field Contract
610327 | Project A | Area3 | Sub Area 31 | Section 311 | C-10192 | 12c14awg Cu 600V TECK, Random Fill | M | 43 | Tray | Field | Field Contract
610328 | Project A | Area3 | Sub Area 31 | Section 311 | C-10193 | 12c14awg Cu 600V TECK, Random Fill | M | 14 | Tray | Field | Field Contract
610329 | Project A | Area3 | Sub Area 31 | Section 311 | C-10194 | 12c14awg Cu 600V TECK, Random Fill | M | 16 | Tray | Field | Field Contract
610330 | Project A | Area3 | Sub Area 31 | Section 311 | C-10195 | 12c14awg Cu 600V TECK, Random Fill | M | 50 | Tray | Field | Field Contract
610331 | Project A | Area3 | Sub Area 31 | Section 311 | C-10196 | 12c14awg Cu 600V TECK, Random Fill | M | 53 | Tray | Field | Field Contract
610332 | Project A | Area3 | Sub Area 31 | Section 311 | C-10197 | 12c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610333 | Project A | Area3 | Sub Area 31 | Section 311 | C-10198 | 12c14awg Cu 600V TECK, Random Fill | M | 29 | Tray | Field | Field Contract
610334 | Project A | Area3 | Sub Area 31 | Section 311 | C-10199 | 12c14awg Cu 600V TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610335 | Project A | Area3 | Sub Area 31 | Section 311 | C-10200 | 12c14awg Cu 600V TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610336 | Project A | Area3 | Sub Area 31 | Section 311 | C-10201 | 12c14awg Cu 600V TECK, Random Fill | M | 126 | Tray | Field | Field Contract
610337 | Project A | Area3 | Sub Area 31 | Section 311 | C-10202 | 12c14awg Cu 600V TECK, Random Fill | M | 126 | Tray | Field | Field Contract
610338 | Project A | Area3 | Sub Area 31 | Section 311 | C-10203 | 12c14awg Cu 600V TECK, Random Fill | M | 143 | Tray | Field | Field Contract
610339 | Project A | Area3 | Sub Area 31 | Section 311 | C-10204 | 12c14awg Cu 600V TECK, Random Fill | M | 143 | Tray | Field | Field Contract
610340 | Project A | Area3 | Sub Area 31 | Section 311 | C-10205 | 12c14awg Cu 600V TECK, Random Fill | M | 41 | Tray | Field | Field Contract
610341 | Project A | Area3 | Sub Area 31 | Section 311 | C-10206 | 12c14awg Cu 600V TECK, Random Fill | M | 41 | Tray | Field | Field Contract
610342 | Project A | Area3 | Sub Area 31 | Section 311 | C-10207 | 12c14awg Cu 600V TECK, Random Fill | M | 41 | Tray | Field | Field Contract
610343 | Project A | Area3 | Sub Area 31 | Section 311 | C-10208 | 12c14awg Cu 600V TECK, Random Fill | M | 41 | Tray | Field | Field Contract
610344 | Project A | Area3 | Sub Area 31 | Section 311 | C-10209 | 12c14awg Cu 600V TECK, Random Fill | M | 48 | Tray | Field | Field Contract
610345 | Project A | Area3 | Sub Area 31 | Section 311 | C-10210 | 12c14awg Cu 600V TECK, Random Fill | M | 11 | Tray | Field | Field Contract
610346 | Project A | Area3 | Sub Area 31 | Section 311 | C-10211 | 12c14awg Cu 600V TECK, Random Fill | M | 13 | Tray | Field | Field Contract
610347 | Project A | Area3 | Sub Area 31 | Section 311 | C-10212 | 1c6awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610348 | Project A | Area3 | Sub Area 31 | Section 311 | C-10213 | 1pr16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610349 | Project A | Area3 | Sub Area 31 | Section 311 | C-10214 | 2c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610350 | Project A | Area3 | Sub Area 31 | Section 311 | C-10215 | 1c6awg Cu 600V TECK, Random Fill | M | 25 | Tray | Module | Module Contract
610351 | Project A | Area3 | Sub Area 31 | Section 311 | C-10216 | 1pr16awg Shld 600V ACIC, Random Fill | M | 25 | Tray | Module | Module Contract
610352 | Project A | Area3 | Sub Area 31 | Section 311 | C-10217 | 2c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Module | Module Contract
610353 | Project A | Area3 | Sub Area 32 | Section 312 | C-10218 | 2pr16awg Shld 300V ACIC, Random Fill | M | 43 | Tray | Field | Field Contract
610354 | Project A | Area3 | Sub Area 32 | Section 312 | C-10219 | 4pr16awg Shld 300V ACIC, Random Fill | M | 11 | Tray | Field | Field Contract
610355 | Project A | Area3 | Sub Area 32 | Section 312 | C-10220 | 4pr16awg Shld 300V ACIC, Random Fill | M | 11 | Tray | Field | Field Contract
610356 | Project A | Area3 | Sub Area 32 | Section 312 | P-10205 | 1pr16awg Shld 300V ACIC, Random Fill | M | 80 | Tray | Field | Field Contract
610357 | Project A | Area3 | Sub Area 32 | Section 312 | P-10206 | 1pr16awg Shld 300V ACIC, Random Fill | M | 80 | Tray | Field | Field Contract
610358 | Project A | Area3 | Sub Area 32 | Section 312 | C-10221 | 1pr16awg Shld 300V ACIC, Random Fill | M | 31 | Tray | Field | Field Contract
610359 | Project A | Area3 | Sub Area 32 | Section 312 | C-10222 | 1pr16awg Shld 300V ACIC, Random Fill | M | 31 | Tray | Field | Field Contract
610360 | Project A | Area3 | Sub Area 32 | Section 312 | C-10223 | 1pr16awg Shld 300V ACIC, Random Fill | M | 49 | Tray | Field | Field Contract
610361 | Project A | Area3 | Sub Area 32 | Section 312 | C-10224 | 1pr16awg Shld 300V ACIC, Random Fill | M | 49 | Tray | Field | Field Contract
610362 | Project A | Area3 | Sub Area 32 | Section 312 | C-10225 | 1pr16awg Shld 300V ACIC, Random Fill | M | 14 | Tray | Field | Field Contract
610363 | Project A | Area3 | Sub Area 32 | Section 312 | C-10226 | 1pr16awg Shld 300V ACIC, Random Fill | M | 23 | Tray | Field | Field Contract
610364 | Project A | Area3 | Sub Area 32 | Section 312 | C-10227 | 1pr16awg Shld 300V ACIC, Random Fill | M | 15 | Tray | Field | Field Contract
610365 | Project A | Area3 | Sub Area 32 | Section 312 | C-10228 | 1pr16awg Shld 300V ACIC, Random Fill | M | 95 | Tray | Field | Field Contract
610366 | Project A | Area3 | Sub Area 32 | Section 312 | C-10229 | 1pr16awg Shld 300V ACIC, Random Fill | M | 82 | Tray | Field | Field Contract
610367 | Project A | Area3 | Sub Area 32 | Section 312 | C-10230 | 1pr16awg Shld 300V ACIC, Random Fill | M | 92 | Tray | Field | Field Contract
610368 | Project A | Area3 | Sub Area 32 | Section 312 | C-10231 | 1pr16awg Shld 300V ACIC, Random Fill | M | 126 | Tray | Field | Field Contract
610369 | Project A | Area3 | Sub Area 32 | Section 312 | C-10232 | 1pr16awg Shld 300V ACIC, Random Fill | M | 100 | Tray | Field | Field Contract
610370 | Project A | Area3 | Sub Area 32 | Section 312 | C-10233 | 1pr16awg Shld 300V ACIC, Random Fill | M | 126 | Tray | Field | Field Contract
610371 | Project A | Area3 | Sub Area 32 | Section 312 | C-10234 | 1pr16awg Shld 300V ACIC, Random Fill | M | 143 | Tray | Field | Field Contract
610372 | Project A | Area3 | Sub Area 32 | Section 312 | C-10235 | 1pr16awg Shld 300V ACIC, Random Fill | M | 143 | Tray | Field | Field Contract
610373 | Project A | Area3 | Sub Area 32 | Section 312 | C-10236 | 1pr16awg Shld 300V ACIC, Random Fill | M | 132 | Tray | Field | Field Contract
610374 | Project A | Area3 | Sub Area 32 | Section 312 | C-10237 | 1pr16awg Shld 300V ACIC, Random Fill | M | 143 | Tray | Field | Field Contract
610375 | Project A | Area3 | Sub Area 32 | Section 312 | C-10238 | 1pr16awg Shld 300V ACIC, Random Fill | M | 143 | Tray | Field | Field Contract
610376 | Project A | Area3 | Sub Area 32 | Section 312 | C-10239 | 1pr16awg Shld 300V ACIC, Random Fill | M | 143 | Tray | Field | Field Contract
610377 | Project A | Area3 | Sub Area 32 | Section 312 | C-10240 | 1pr16awg Shld 300V ACIC, Random Fill | M | 18 | Tray | Field | Field Contract
610378 | Project A | Area3 | Sub Area 32 | Section 312 | C-10241 | 1pr16awg Shld 300V ACIC, Random Fill | M | 18 | Tray | Field | Field Contract
610379 | Project A | Area3 | Sub Area 32 | Section 312 | C-10242 | 1pr16awg Shld 300V ACIC, Random Fill | M | 18 | Tray | Field | Field Contract
610380 | Project A | Area3 | Sub Area 32 | Section 312 | C-10243 | 1pr16awg Shld 300V ACIC, Random Fill | M | 20 | Tray | Field | Field Contract
610381 | Project A | Area3 | Sub Area 32 | Section 312 | C-10244 | 1pr16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610382 | Project A | Area3 | Sub Area 32 | Section 312 | C-10245 | 1pr16awg Shld 300V ACIC, Random Fill | M | 23 | Tray | Field | Field Contract
610383 | Project A | Area3 | Sub Area 32 | Section 312 | C-10246 | 1pr16awg Shld 300V ACIC, Random Fill | M | 23 | Tray | Field | Field Contract
610384 | Project A | Area3 | Sub Area 32 | Section 312 | C-10247 | 1pr16awg Shld 300V ACIC, Random Fill | M | 23 | Tray | Field | Field Contract
610385 | Project A | Area3 | Sub Area 32 | Section 312 | C-10248 | 1pr16awg Shld 300V ACIC, Random Fill | M | 18 | Tray | Field | Field Contract
610386 | Project A | Area3 | Sub Area 32 | Section 312 | C-10249 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610387 | Project A | Area3 | Sub Area 32 | Section 312 | C-10250 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610388 | Project A | Area3 | Sub Area 32 | Section 312 | C-10251 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610389 | Project A | Area3 | Sub Area 32 | Section 312 | C-10252 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Field | Field Contract
610390 | Project A | Area3 | Sub Area 32 | Section 312 | C-10253 | 1pr16awg Shld 300V ACIC, Random Fill | M | 11 | Tray | Field | Field Contract
610391 | Project A | Area3 | Sub Area 32 | Section 312 | C-10254 | 1pr16awg Shld 300V ACIC, Random Fill | M | 15 | Tray | Field | Field Contract
610392 | Project A | Area3 | Sub Area 32 | Section 312 | C-10255 | 1pr16awg Shld 300V ACIC, Random Fill | M | 11 | Tray | Field | Field Contract
610393 | Project A | Area3 | Sub Area 32 | Section 312 | P-10127 | 2c10awg Cu 600V TECK, Random Fill | M | 10 | Tray | Field | Field Contract
610394 | Project A | Area3 | Sub Area 32 | Section 312 | C-10256 | 6c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Field | Field Contract
610395 | Project A | Area3 | Sub Area 32 | Section 312 | C-10257 | 6c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Field | Field Contract
610396 | Project A | Area3 | Sub Area 32 | Section 312 | C-10258 | 6c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Field | Field Contract
610397 | Project A | Area3 | Sub Area 32 | Section 312 | C-10259 | 6c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Field | Field Contract
610398 | Project A | Area3 | Sub Area 32 | Section 312 | C-10260 | 6c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Field | Field Contract
610399 | Project A | Area3 | Sub Area 32 | Section 312 | C-10261 | 6c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Field | Field Contract
610400 | Project A | Area3 | Sub Area 32 | Section 312 | P-10128 | 2c10awg Cu 600V TECK, Random Fill | M | 10 | Tray | Field | Field Contract
610401 | Project A | Area3 | Sub Area 32 | Section 312 | P-10129 | 2c10awg Cu 600V TECK, Random Fill | M | 10 | Tray | Field | Field Contract
610402 | Project A | Area3 | Sub Area 32 | Section 312 | P-10130 | 2c10awg Cu 600V TECK, Random Fill | M | 5 | Tray | Field | Field Contract
610403 | Project A | Area3 | Sub Area 32 | Section 312 | P-10131 | 2c10awg Cu 600V TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610404 | Project A | Area3 | Sub Area 32 | Section 312 | P-10132 | 2c10awg Cu 600V TECK, Random Fill | M | 45 | Tray | Field | Field Contract
610405 | Project A | Area3 | Sub Area 32 | Section 312 | P-10133 | 2c10awg Cu 600V TECK, Random Fill | M | 50 | Tray | Field | Field Contract
610406 | Project A | Area3 | Sub Area 32 | Section 312 | P-10134 | 2c10awg | M | 70 | Tray | Field | Field Contract
610407 | Project A | Area3 | Sub Area 32 | Section 312 | P-10136 | 2c10awg | M | 15 | Tray | Field | Field Contract
610408 | Project A | Area3 | Sub Area 32 | Section 312 | P-10137 | 2c10awg Cu 600V TECK, Random Fill | M | 5 | Tray | Field | Field Contract
610409 | Project A | Area3 | Sub Area 32 | Section 312 | P-10138 | 2c10awg Cu 600V TECK, Random Fill | M | 14 | Tray | Field | Field Contract
610410 | Project A | Area3 | Sub Area 32 | Section 312 | P-10139 | 2c10awg Cu 600V TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610411 | Project A | Area3 | Sub Area 32 | Section 312 | P-10140 | 2c10awg Cu 600V TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610412 | Project A | Area3 | Sub Area 32 | Section 312 | P-10141 | 2c10awg Cu 600V TECK, Random Fill | M | 13 | Tray | Field | Field Contract
610413 | Project A | Area3 | Sub Area 32 | Section 312 | P-10142 | 2c10awg Cu 600V TECK, Random Fill | M | 16 | Tray | Field | Field Contract
610414 | Project A | Area3 | Sub Area 32 | Section 312 | P-10143 | 2c10awg Cu 600V TECK, Random Fill | M | 31 | Tray | Field | Field Contract
610415 | Project A | Area4 | Sub Area 41 | Section 411 | C-10262 | 6pr16awg Shld 300V ACIC, Random Fill | M | 76 | Tray | Field | Field Contract
610416 | Project A | Area4 | Sub Area 41 | Section 411 | C-10263 | 20c14awg Cu 600V TECK, Random Fill | M | 76 | Tray | Field | Field Contract
610417 | Project A | Area4 | Sub Area 41 | Section 411 | C-10264 | 20c14awg Cu 600V TECK, Random Fill | M | 76 | Tray | Field | Field Contract
610418 | Project A | Area4 | Sub Area 41 | Section 411 | C-10265 | 20c14awg Cu 600V TECK, Random Fill | M | 76 | Tray | Field | Field Contract
610419 | Project A | Area4 | Sub Area 41 | Section 411 | C-10266 | 20c14awg Cu 600V TECK, Random Fill | M | 76 | Tray | Field | Field Contract
610420 | Project A | Area4 | Sub Area 41 | Section 411 | C-10267 | 20c14awg Cu 600V TECK, Random Fill | M | 76 | Tray | Field | Field Contract
610421 | Project A | Area4 | Sub Area 41 | Section 411 | C-10268 | 20c14awg Cu 600V TECK, Random Fill | M | 76 | Tray | Field | Field Contract
610422 | Project A | Area4 | Sub Area 41 | Section 411 | C-10269 | 20c14awg Cu 600V TECK, Random Fill | M | 76 | Tray | Field | Field Contract
610423 | Project A | Area4 | Sub Area 41 | Section 411 | C-10270 | 8pr16awg Shld 300V ACIC, Random Fill | M | 290 | Tray | Field | Field Contract
610424 | Project A | Area4 | Sub Area 41 | Section 411 | C-10271 | 4pr16awg Shld 300V ACIC, Random Fill | M | 290 | Tray | Field | Field Contract
610425 | Project A | Area4 | Sub Area 41 | Section 411 | C-10272 | 4triad 16awg Shld 300V ACIC, Random Fill | M | 290 | Tray | Field | Field Contract
610426 | Project A | Area4 | Sub Area 41 | Section 411 | C-10273 | 20c14awg Cu 600V TECK, Random Fill | M | 290 | Tray | Field | Field Contract
610427 | Project A | Area4 | Sub Area 41 | Section 411 | C-10274 | 20c14awg Cu 600V TECK, Random Fill | M | 156 | Tray | Field | Field Contract
610428 | Project A | Area4 | Sub Area 41 | Section 411 | C-10275 | 8pr16awg Shld 300V ACIC, Random Fill | M | 152 | Tray | Field | Field Contract
610429 | Project A | Area4 | Sub Area 41 | Section 411 | C-10276 | 20c14awg Cu 600V TECK, Random Fill | M | 152 | Tray | Field | Field Contract
610430 | Project A | Area4 | Sub Area 41 | Section 411 | C-10277 | 20c14awg Cu 600V TECK, Random Fill | M | 152 | Tray | Field | Field Contract
610431 | Project A | Area4 | Sub Area 41 | Section 411 | C-10278 | 20c14awg Cu 600V TECK, Random Fill | M | 152 | Tray | Field | Field Contract
610432 | Project A | Area4 | Sub Area 41 | Section 411 | C-10279 | 20c14awg Cu 600V TECK, Random Fill | M | 152 | Tray | Field | Field Contract
610433 | Project A | Area4 | Sub Area 41 | Section 411 | C-10280 | 6pr16awg Shld 300V ACIC, Random Fill | M | 178 | Tray | Field | Field Contract
610434 | Project A | Area4 | Sub Area 41 | Section 411 | C-10281 | 30c14awg Cu 600V TECK, Random Fill | M | 184 | Tray | Field | Field Contract
610435 | Project A | Area4 | Sub Area 41 | Section 411 | C-10282 | 4c14awg | M | 5 | Tray | Module | Module Contract
610436 | Project A | Area4 | Sub Area 41 | Section 411 | C-10283 | 4c14awg | M | 5 | Tray | Module | Module Contract
610437 | Project A | Area4 | Sub Area 41 | Section 411 | C-10284 | 4c14awg | M | 10 | Tray | Module | Module Contract
610438 | Project A | Area4 | Sub Area 41 | Section 411 | C-10285 | 2c14awg | M | 18 | Tray | Module | Module Contract
610439 | Project A | Area4 | Sub Area 41 | Section 411 | C-10286 | 4c14awg | M | 25 | Tray | Module | Module Contract
610440 | Project A | Area4 | Sub Area 41 | Section 411 | C-10287 | 4pr16awg Shld 300V ACIC, Random Fill | M | 166 | Tray | Field | Field Contract
610441 | Project A | Area4 | Sub Area 41 | Section 411 | C-10288 | 20c14awg Cu 600V TECK, Random Fill | M | 166 | Tray | Field | Field Contract
610442 | Project A | Area4 | Sub Area 41 | Section 411 | C-10289 | 20c14awg Cu 600V TECK, Random Fill | M | 166 | Tray | Field | Field Contract
610443 | Project A | Area4 | Sub Area 41 | Section 411 | C-10290 | 20c14awg Cu 600V TECK, Random Fill | M | 166 | Tray | Field | Field Contract
610444 | Project A | Area4 | Sub Area 41 | Section 411 | C-10291 | 20c14awg Cu 600V TECK, Random Fill | M | 85 | Tray | Field | Field Contract
610445 | Project A | Area4 | Sub Area 41 | Section 411 | C-10292 | 20c14awg Cu 600V TECK, Random Fill | M | 85 | Tray | Field | Field Contract
610446 | Project A | Area4 | Sub Area 41 | Section 411 | C-10293 | 20c14awg Cu 600V TECK, Random Fill | M | 85 | Tray | Field | Field Contract
610447 | Project A | Area4 | Sub Area 41 | Section 411 | C-10294 | 20c14awg Cu 600V TECK, Random Fill | M | 85 | Tray | Field | Field Contract
610448 | Project A | Area4 | Sub Area 41 | Section 411 | C-10295 | 20c14awg Cu 600V TECK, Random Fill | M | 85 | Tray | Field | Field Contract
610449 | Project A | Area4 | Sub Area 41 | Section 411 | C-10296 | 20c14awg Cu 600V TECK, Random Fill | M | 85 | Tray | Field | Field Contract
610450 | Project A | Area4 | Sub Area 41 | Section 411 | C-10297 | 20c14awg Cu 600V TECK, Random Fill | M | 85 | Tray | Field | Field Contract
610451 | Project A | Area4 | Sub Area 41 | Section 411 | C-10298 | 8pr16awg Shld 300V ACIC, Random Fill | M | 85 | Tray | Field | Field Contract
610452 | Project A | Area4 | Sub Area 41 | Section 411 | C-10299 | 8pr16awg Shld 300V ACIC, Random Fill | M | 85 | Tray | Field | Field Contract
610453 | Project A | Area4 | Sub Area 41 | Section 411 | C-10300 | 4pr16awg Shld 300V ACIC, Random Fill | M | 85 | Tray | Field | Field Contract
610454 | Project A | Area4 | Sub Area 41 | Section 411 | C-10301 | 8triad 16awg 300V ACIC, Random Fill | M | 85 | Tray | Field | Field Contract
610455 | Project A | Area4 | Sub Area 41 | Section 411 | C-10302 | 8triad 16awg 300V ACIC, Random Fill | M | 85 | Tray | Field | Field Contract
610456 | Project A | Area4 | Sub Area 41 | Section 411 | C-10303 | 6pr16awg Shld 300V ACIC, Random Fill | M | 100 | Tray | Field | Field Contract
610457 | Project A | Area4 | Sub Area 41 | Section 411 | C-10304 | 20c14awg Cu 600V TECK, Random Fill | M | 81 | Tray | Field | Field Contract
610458 | Project A | Area4 | Sub Area 41 | Section 411 | C-10305 | 6pr16awg Shld 300V ACIC, Random Fill | M | 126 | Tray | Field | Field Contract
610459 | Project A | Area4 | Sub Area 41 | Section 411 | C-10306 | 20c14awg Cu 600V TECK, Random Fill | M | 97 | Tray | Field | Field Contract
610460 | Project A | Area4 | Sub Area 41 | Section 411 | C-10307 | 6pr16awg Shld 300V ACIC, Random Fill | M | 138 | Tray | Field | Field Contract
610461 | Project A | Area4 | Sub Area 41 | Section 411 | C-10308 | 20c14awg Cu 600V TECK, Random Fill | M | 132 | Tray | Field | Field Contract
610462 | Project A | Area4 | Sub Area 41 | Section 411 | C-10309 | 8pr16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610463 | Project A | Area4 | Sub Area 41 | Section 411 | C-10310 | 4triad 16awg Shld 300V ACIC, Random Fill | M | 25 | Tray | Field | Field Contract
610464 | Project A | Area4 | Sub Area 41 | Section 411 | C-10311 | 20c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610465 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10003 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610466 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10004 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610467 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10005 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610468 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10006 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610469 | Project A | Area4 | Sub Area 41 | Section 411 | C-10312 | 10c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610470 | Project A | Area4 | Sub Area 41 | Section 411 | C-10313 | 4c14awg CU 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610471 | Project A | Area4 | Sub Area 41 | Section 411 | C-10314 | 4c14awg CU 600V TECK, Random Fill | M | 12 | Tray | Module | Module Contract
610472 | Project A | Area4 | Sub Area 41 | Section 411 | C-10315 | 4c14awg CU 600V TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610473 | Project A | Area4 | Sub Area 41 | Section 411 | C-10316 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Module | Module Contract
610474 | Project A | Area4 | Sub Area 41 | Section 411 | C-10317 | 1pr16awg Shld 300V ACIC, Random Fill | M | 10 | Tray | Module | Module Contract
610475 | Project A | Area4 | Sub Area 41 | Section 411 | C-10318 | 1pr16awg Shld 300V ACIC, Random Fill | M | 5 | Tray | Module | Module Contract
610476 | Project A | Area4 | Sub Area 41 | Section 411 | C-10319 | 1pr16awg Shld 300V ACIC, Random Fill | M | 15 | Tray | Module | Module Contract
610477 | Project A | Area4 | Sub Area 42 | Section 412 | C-10320 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610478 | Project A | Area4 | Sub Area 42 | Section 412 | C-10321 | 2c14awg Cu 600V TECK, Random Fill | M | 11 | Tray | Module | Module Contract
610479 | Project A | Area4 | Sub Area 42 | Section 412 | C-10322 | 2c14awg Cu 600V TECK, Random Fill | M | 11 | Tray | Module | Module Contract
610480 | Project A | Area4 | Sub Area 42 | Section 412 | C-10323 | 2c14awg Cu 600V TECK, Random Fill | M | 11 | Tray | Module | Module Contract
610481 | Project A | Area4 | Sub Area 42 | Section 412 | C-10324 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610482 | Project A | Area4 | Sub Area 42 | Section 412 | C-10325 | 2c14awg Cu 600V TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610483 | Project A | Area4 | Sub Area 42 | Section 412 | C-10326 | 2c14awg Cu 600V TECK, Random Fill | M | 16 | Tray | Module | Module Contract
610484 | Project A | Area4 | Sub Area 42 | Section 412 | C-10327 | 2c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Module | Module Contract
610485 | Project A | Area4 | Sub Area 42 | Section 412 | C-10328 | 20c14awg Cu 600V TECK, Random Fill | M | 333 | Tray | Field | Field Contract
610486 | Project A | Area4 | Sub Area 42 | Section 412 | C-10329 | 6c14awg Cu 600V TECK, Random Fill | M | 23 | Tray | Field | Field Contract
610487 | Project A | Area4 | Sub Area 42 | Section 412 | C-10330 | 6c14awg Cu 600V TECK, Random Fill | M | 30 | Tray | Field | Field Contract
610488 | Project A | Area4 | Sub Area 42 | Section 412 | C-10331 | 6c14awg Cu 600V TECK, Random Fill | M | 13 | Tray | Field | Field Contract
610489 | Project A | Area4 | Sub Area 42 | Section 412 | C-10332 | 6c14awg Cu 600V TECK, Random Fill | M | 30 | Tray | Field | Field Contract
610490 | Project A | Area4 | Sub Area 42 | Section 412 | C-10333 | 6c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610491 | Project A | Area4 | Sub Area 42 | Section 412 | C-10334 | 10c14awg Cu 600V TECK, Random Fill | M | 10 | Tray | Field | Field Contract
610492 | Project A | Area4 | Sub Area 42 | Section 412 | C-10335 | 10c14awg Cu 600V TECK, Random Fill | M | 10 | Tray | Field | Field Contract
610493 | Project A | Area4 | Sub Area 42 | Section 412 | C-10336 | 4c14awg CU 600V TECK, Random Fill | M | 47 | Tray | Field | Field Contract
610494 | Project A | Area4 | Sub Area 42 | Section 412 | C-10337 | 4c14awg CU 600V TECK, Random Fill | M | 14 | Tray | Field | Field Contract
610495 | Project A | Area4 | Sub Area 42 | Section 412 | C-10338 | 4c14awg CU 600V TECK, Random Fill | M | 23 | Tray | Field | Field Contract
610496 | Project A | Area4 | Sub Area 42 | Section 412 | C-10339 | 4c14awg CU 600V TECK, Random Fill | M | 18 | Tray | Field | Field Contract
610497 | Project A | Area4 | Sub Area 42 | Section 412 | C-10340 | 4c14awg CU 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610498 | Project A | Area4 | Sub Area 42 | Section 412 | CAT-10007 | Cat6e | M | 25 | Tray | Module | Module Contract
610499 | Project A | Area4 | Sub Area 42 | Section 412 | C-10341 | 1pr16awg, Unarmored | M | 31 | Tray | Field | Field Contract
610500 | Project A | Area4 | Sub Area 42 | Section 412 | C-10342 | 1pr16awg, Unarmored | M | 31 | Tray | Field | Field Contract
610501 | Project A | Area4 | Sub Area 42 | Section 412 | C-10343 | 1pr16awg, Unarmored | M | 55 | Tray | Field | Field Contract
610502 | Project A | Area4 | Sub Area 42 | Section 412 | C-10344 | 1pr16awg, Unarmored | M | 14 | Tray | Field | Field Contract
610503 | Project A | Area4 | Sub Area 42 | Section 412 | C-10345 | 10c14awg | M | 5 | Tray | Module | Module Contract
610504 | Project A | Area4 | Sub Area 42 | Section 412 | C-10346 | 10c14awg | M | 5 | Tray | Module | Module Contract
610505 | Project A | Area4 | Sub Area 42 | Section 412 | C-10347 | 10c14awg | M | 5 | Tray | Module | Module Contract
610506 | Project A | Area4 | Sub Area 42 | Section 412 | C-10348 | 10c14awg | M | 5 | Tray | Module | Module Contract
610507 | Project A | Area4 | Sub Area 42 | Section 412 | B-10006 | 2c6awg | M | 38 | DirBuried | Field | Field Contract
610508 | Project A | Area4 | Sub Area 42 | Section 412 | B-10007 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 38 | DirBuried | Field | Field Contract
610509 | Project A | Area4 | Sub Area 42 | Section 412 | B-10008 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 38 | DirBuried | Field | Field Contract
610510 | Project A | Area4 | Sub Area 42 | Section 412 | B-10009 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 38 | DirBuried | Field | Field Contract
610511 | Project A | Area4 | Sub Area 42 | Section 412 | B-10010 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 38 | DirBuried | Field | Field Contract
610512 | Project A | Area4 | Sub Area 42 | Section 412 | B-10011 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 38 | DirBuried | Field | Field Contract
610513 | Project A | Area4 | Sub Area 42 | Section 412 | B-10012 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 38 | DirBuried | Field | Field Contract
610514 | Project A | Area4 | Sub Area 42 | Section 412 | C-10350 | 2c6awg Cu 1kV TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610515 | Project A | Area4 | Sub Area 42 | Section 412 | P-10155 | 3c250mcm Cu 1kV TECK | M | 15 | Tray | Field | Field Contract
610516 | Project A | Area4 | Sub Area 42 | Section 412 | P-10156 | 3c250mcm Cu 1kV TECK | M | 15 | Tray | Field | Field Contract
610517 | Project A | Area4 | Sub Area 42 | Section 412 | P-10157 | 3c250mcm Cu 1kV TECK | M | 15 | Tray | Field | Field Contract
610518 | Project A | Area4 | Sub Area 42 | Section 412 | P-10158 | 4c300mcm Cu 1kV CONDUIT, Random Fill | M | 5 | Tray | Module | Module Contract
610519 | Project A | Area4 | Sub Area 42 | Section 412 | P-10159 | 4c300mcm Cu 1kV CONDUIT, Random Fill | M | 5 | Tray | Module | Module Contract
610520 | Project A | Area4 | Sub Area 42 | Section 412 | C-10351 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610521 | Project A | Area4 | Sub Area 42 | Section 412 | C-10352 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610522 | Project A | Area4 | Sub Area 42 | Section 412 | C-10353 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610523 | Project A | Area4 | Sub Area 42 | Section 412 | C-10354 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610524 | Project A | Area4 | Sub Area 42 | Section 412 | P-10160 | 2c8awg Cu 1kV TECK, Random Fill | M | 345 | Tray | Field | Field Contract
610525 | Project A | Area4 | Sub Area 42 | Section 412 | P-10161 | 2c12awg | M | 28 | Tray | Module | Module Contract
610526 | Project A | Area4 | Sub Area 42 | Section 412 | P-10162 | 4c12awg | M | 10 | Tray | Module | Module Contract
610527 | Project A | Area4 | Sub Area 42 | Section 412 | P-10163 | 2c12awg | M | 12 | Tray | Module | Module Contract
610528 | Project A | Area4 | Sub Area 42 | Section 412 | P-10164 | 2c12awg | M | 15 | Tray | Module | Module Contract
610529 | Project A | Area4 | Sub Area 42 | Section 412 | P-10165 | 2c12awg | M | 10 | Tray | Module | Module Contract
610530 | Project A | Area4 | Sub Area 42 | Section 412 | P-10166 | 2c12awg | M | 11 | Tray | Module | Module Contract
610531 | Project A | Area4 | Sub Area 42 | Section 412 | P-10167 | 2c12awg | M | 12 | Tray | Module | Module Contract
610532 | Project A | Area4 | Sub Area 42 | Section 412 | P-10168 | 2c12awg | M | 10 | Tray | Module | Module Contract
610533 | Project A | Area4 | Sub Area 42 | Section 412 | P-10169 | 2c12awg | M | 15 | Tray | Module | Module Contract
610534 | Project A | Area4 | Sub Area 42 | Section 412 | P-10170 | 4c12awg CU 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610535 | Project A | Area4 | Sub Area 42 | Section 412 | P-10171 | 6c12awg Cu 600V TECK, Random Fill | M | 13 | Tray | Module | Module Contract
610536 | Project A | Area4 | Sub Area 42 | Section 412 | P-10172 | 2c12awg Cu 600V TECK, Random Fill | M | 16 | Tray | Module | Module Contract
610537 | Project A | Area4 | Sub Area 42 | Section 412 | P-10173 | 2c12awg Cu 600V TECK, Random Fill | M | 24 | Tray | Module | Module Contract
610538 | Project A | Area4 | Sub Area 42 | Section 412 | P-10174 | 2c12awg Cu 600V TECK, Random Fill | M | 28 | Tray | Module | Module Contract
610539 | Project A | Area4 | Sub Area 42 | Section 412 | C-10355 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610540 | Project A | Area4 | Sub Area 42 | Section 412 | C-10356 | 6c14awg Cu 600V TECK, Random Fill | M | 10 | Tray | Module | Module Contract
610541 | Project A | Area4 | Sub Area 42 | Section 412 | P-10175 | 2c1/0awg Cu 1kV TECK | M | 10 | Tray | Module | Module Contract
610542 | Project A | Area4 | Sub Area 42 | Section 412 | CAT-10008 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 12 | Tray | Module | Module Contract
610543 | Project A | Area4 | Sub Area 43 | Section 413 | C-10357 | 30c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610544 | Project A | Area4 | Sub Area 43 | Section 413 | C-10358 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610545 | Project A | Area4 | Sub Area 43 | Section 413 | P-10177 | 2c2awg Cu 1kV TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610546 | Project A | Area4 | Sub Area 43 | Section 413 | C-10359 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610547 | Project A | Area4 | Sub Area 43 | Section 413 | P-10178 | 3c2awg Cu 1kV TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610548 | Project A | Area4 | Sub Area 43 | Section 413 | P-10179 | 2c2awg Cu 1kV TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610549 | Project A | Area4 | Sub Area 43 | Section 413 | C-10360 | 2c14awg Cu 600V TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610550 | Project A | Area4 | Sub Area 43 | Section 413 | C-10361 | 4c14awg CU 600V TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610551 | Project A | Area4 | Sub Area 43 | Section 413 | C-10362 | 8triad 16awg 300V ACIC, Random Fill | M | 138 | Tray | Field | Field Contract
610552 | Project A | Area4 | Sub Area 43 | Section 413 | C-10363 | 8triad 16awg 300V ACIC, Random Fill | M | 138 | Tray | Field | Field Contract
610553 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10009 | Cat6e | M | 18 | Tray | Module | Module Contract
610554 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10010 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 18 | Tray | Module | Module Contract
610555 | Project A | Area4 | Sub Area 43 | Section 413 | C-10364 | 4c14awg | M | 14 | Tray | Module | Module Contract
610556 | Project A | Area4 | Sub Area 43 | Section 413 | C-10365 | 4c14awg CU 600V TECK, Random Fill | M | 14 | Tray | Module | Module Contract
610557 | Project A | Area4 | Sub Area 43 | Section 413 | C-10366 | 4pr16awg Shld 300V ACIC, Random Fill | M | 17 | Tray | Module | Module Contract
610558 | Project A | Area4 | Sub Area 43 | Section 413 | C-10367 | 40c14awg Cu 600V TECK, Random Fill | M | 17 | Tray | Module | Module Contract
610559 | Project A | Area4 | Sub Area 43 | Section 413 | P-10182 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 85 | Tray | Field | Field Contract
610560 | Project A | Area4 | Sub Area 43 | Section 413 | P-10183 | 3c10awg Cu 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610561 | Project A | Area4 | Sub Area 43 | Section 413 | C-10368 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610562 | Project A | Area4 | Sub Area 43 | Section 413 | C-10369 | 4c14awg CU 600V TECK, Random Fill | M | 120 | Tray | Field | Field Contract
610563 | Project A | Area4 | Sub Area 43 | Section 413 | C-10370 | 8triad 16awg 300V ACIC, Random Fill | M | 149 | Tray | Field | Field Contract
610564 | Project A | Area4 | Sub Area 43 | Section 413 | C-10371 | 8triad 16awg 300V ACIC, Random Fill | M | 149 | Tray | Field | Field Contract
610565 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10011 | Cat6e | M | 23 | Tray | Module | Module Contract
610566 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10012 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 23 | Tray | Module | Module Contract
610567 | Project A | Area4 | Sub Area 43 | Section 413 | C-10372 | 4c14awg CU 600V TECK, Random Fill | M | 18 | Tray | Module | Module Contract
610568 | Project A | Area4 | Sub Area 43 | Section 413 | C-10373 | 4c14awg CU 600V TECK, Random Fill | M | 18 | Tray | Module | Module Contract
610569 | Project A | Area4 | Sub Area 43 | Section 413 | C-10374 | 4pr16awg Shld 300V ACIC, Random Fill | M | 22 | Tray | Module | Module Contract
610570 | Project A | Area4 | Sub Area 43 | Section 413 | C-10375 | 40c14awg Cu 600V TECK, Random Fill | M | 22 | Tray | Module | Module Contract
610571 | Project A | Area4 | Sub Area 43 | Section 413 | P-10186 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 100 | Tray | Field | Field Contract
610572 | Project A | Area4 | Sub Area 43 | Section 413 | P-10187 | 3c10awg Cu 600V TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610573 | Project A | Area4 | Sub Area 43 | Section 413 | C-10376 | 2c14awg Cu 600V TECK, Random Fill | M | 5 | Tray | Module | Module Contract
610574 | Project A | Area4 | Sub Area 43 | Section 413 | C-10377 | 4c14awg CU 600V TECK, Random Fill | M | 132 | Tray | Field | Field Contract
610575 | Project A | Area4 | Sub Area 43 | Section 413 | C-10378 | 8triad 16awg 300V ACIC, Random Fill | M | 161 | Tray | Field | Field Contract
610576 | Project A | Area4 | Sub Area 43 | Section 413 | C-10379 | 8triad 16awg 300V ACIC, Random Fill | M | 161 | Tray | Field | Field Contract
610577 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10013 | Cat6e | M | 23 | Tray | Module | Module Contract
610578 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10014 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 23 | Tray | Module | Module Contract
610579 | Project A | Area4 | Sub Area 43 | Section 413 | C-10380 | 4c14awg CU 600V TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610580 | Project A | Area4 | Sub Area 43 | Section 413 | C-10381 | 4c14awg CU 600V TECK, Random Fill | M | 15 | Tray | Module | Module Contract
610581 | Project A | Area4 | Sub Area 43 | Section 413 | C-10382 | 4pr16awg Shld 300V ACIC, Random Fill | M | 20 | Tray | Module | Module Contract
610582 | Project A | Area4 | Sub Area 43 | Section 413 | C-10383 | 40c14awg Cu 600V TECK, Random Fill | M | 20 | Tray | Module | Module Contract
610583 | Project A | Area4 | Sub Area 43 | Section 413 | P-10190 | 3c500mcm Cu 5kV Unshld TECK 90C | M | 132 | Tray | Field | Field Contract
610584 | Project A | Area4 | Sub Area 43 | Section 413 | P-10191 | 3c10awg Cu 600V TECK, Random Fill | M | 126 | Tray | Field | Field Contract
610585 | Project A | Area4 | Sub Area 43 | Section 413 | C-10384 | 2pr16awg Shld 300V ACIC, Random Fill | M | 24 | Tray | Field | Field Contract
610586 | Project A | Area4 | Sub Area 43 | Section 413 | C-10385 | 2pr16awg Shld 300V ACIC, Random Fill | M | 24 | Tray | Field | Field Contract
610587 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10015 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610588 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10016 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610589 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10017 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610590 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10018 | Cat6e Ethernet Cable, Armoured, Random Fill | M | 5 | Tray | Module | Module Contract
610591 | Project A | Area4 | Sub Area 43 | Section 413 | C-10386 | 2c14awg Cu 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610592 | Project A | Area4 | Sub Area 43 | Section 413 | C-10387 | 2c14awg Cu 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610593 | Project A | Area4 | Sub Area 43 | Section 413 | C-10388 | 2c14awg Cu 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610594 | Project A | Area4 | Sub Area 43 | Section 413 | C-10389 | 2c14awg Cu 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610595 | Project A | Area4 | Sub Area 43 | Section 413 | C-10390 | 2c14awg Cu 600V TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610596 | Project A | Area4 | Sub Area 43 | Section 413 | C-10391 | 2c14awg Cu 600V TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610597 | Project A | Area4 | Sub Area 43 | Section 413 | C-10392 | 2c14awg Cu 600V TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610598 | Project A | Area4 | Sub Area 43 | Section 413 | C-10393 | 2c14awg Cu 600V TECK, Random Fill | M | 75 | Tray | Field | Field Contract
610599 | Project A | Area4 | Sub Area 43 | Section 413 | C-10394 | 2c14awg Cu 600V TECK, Random Fill | M | 75 | Tray | Field | Field Contract
610600 | Project A | Area4 | Sub Area 43 | Section 413 | C-10395 | 2c14awg Cu 600V TECK, Random Fill | M | 75 | Tray | Field | Field Contract
610601 | Project A | Area4 | Sub Area 43 | Section 413 | C-10396 | 2c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610602 | Project A | Area4 | Sub Area 43 | Section 413 | C-10397 | 2c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610603 | Project A | Area4 | Sub Area 43 | Section 413 | C-10398 | 2c14awg Cu 600V TECK, Random Fill | M | 25 | Tray | Field | Field Contract
610604 | Project A | Area4 | Sub Area 43 | Section 413 | C-10399 | 2c14awg Cu 600V TECK, Random Fill | M | 15 | Tray | Field | Field Contract
610605 | Project A | Area4 | Sub Area 43 | Section 413 | C-10400 | 2c14awg Cu 600V TECK, Random Fill | M | 35 | Tray | Field | Field Contract
610606 | Project A | Area4 | Sub Area 43 | Section 413 | C-10401 | 2c14awg Cu 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610607 | Project A | Area4 | Sub Area 43 | Section 413 | C-10402 | 2c14awg Cu 600V TECK, Random Fill | M | 120 | Tray | Field | Field Contract
610608 | Project A | Area4 | Sub Area 43 | Section 413 | C-10403 | 2c14awg Cu 600V TECK, Random Fill | M | 95 | Tray | Field | Field Contract
610609 | Project A | Area4 | Sub Area 43 | Section 413 | C-10404 | 2c14awg Cu 600V TECK, Random Fill | M | 80 | Tray | Field | Field Contract
610610 | Project A | Area4 | Sub Area 43 | Section 413 | C-10405 | 2c14awg Cu 600V TECK, Random Fill | M | 70 | Tray | Field | Field Contract
610611 | Project A | Area4 | Sub Area 43 | Section 413 | C-10406 | 2c14awg Cu 600V TECK, Random Fill | M | 66 | Tray | Field | Field Contract
Electrical Bulks MTO Input Required - Wire & Cable
Example - Imaginary Project with made up quantities for Illustration Purposes
Go to Tab Index

## Tray MTO Input
MTO_ID | WBS1 | WBS2 | WBS3 | WBS4 | CATEGORY | SUB_CATEGORY | Al/Steel/FRP | Width (inch) | Fitting MTO or Composite | Module_Field | Description | Units | Quantity
620001 | Project A | Area1 | Sub Area 11 | Section 111 | Tray | Al_Tray | AL | 12 | Fitting MTO | Field | Aluminum Ladder Tray | M | 30
620002 | Project A | Area1 | Sub Area 11 | Section 111 | Tray | Al_Tray | AL | 6 | Fitting MTO | Field | Aluminum Ladder Tray | M | 60
620003 | Project A | Area1 | Sub Area 11 | Section 111 | Tray | 90Elbow_Vertical | AL | 12 | Fitting MTO | Field | 90Elbow_Vertical | EA | 2
620004 | Project A | Area1 | Sub Area 11 | Section 111 | Tray | 90Elbow | AL | 12 | Fitting MTO | Field | 90Elbow | EA | 10
620005 | Project A | Area1 | Sub Area 11 | Section 111 | Tray | 90Elbow_Vertical | AL | 6 | Fitting MTO | Field | 90Elbow_Vertical | EA | 4
620006 | Project A | Area1 | Sub Area 11 | Section 111 | Tray | 90Elbow | AL | 6 | Fitting MTO | Field | 90Elbow | EA | 20
620007 | Project A | Area1 | Sub Area 11 | Section 112 | Tray | Al_Tray | AL | 6 | Fitting MTO | Field | Aluminum Ladder Tray | M | 60
620008 | Project A | Area1 | Sub Area 11 | Section 112 | Tray | 90Elbow | AL | 6 | Fitting MTO | Field | 90Elbow | EA | 10
620009 | Project A | Area1 | Sub Area 11 | Section 112 | Tray | 45Elbow | AL | 6 | Fitting MTO | Field | 45Elbow | EA | 10
620010 | Project A | Area2 | Sub Area 21 | Section 211 | Tray | Al_Tray | AL | 24 | Fitting MTO | Field | Aluminum Ladder Tray | M | 20
620011 | Project A | Area2 | Sub Area 21 | Section 211 | Tray | Al_Tray | AL | 6 | Fitting MTO | Field | Aluminum Ladder Tray | M | 240
620012 | Project A | Area2 | Sub Area 21 | Section 211 | Tray | 90Elbow_Vertical | AL | 24 | Fitting MTO | Field | 90Elbow_Vertical | EA | 2
620013 | Project A | Area2 | Sub Area 21 | Section 211 | Tray | 90Elbow | AL | 24 | Fitting MTO | Field | 90Elbow | EA | 4
620014 | Project A | Area2 | Sub Area 21 | Section 211 | Tray | 90Elbow_Vertical | AL | 6 | Fitting MTO | Field | 90Elbow_Vertical | EA | 10
620015 | Project A | Area2 | Sub Area 21 | Section 211 | Tray | 90Elbow | AL | 6 | Fitting MTO | Field | 90Elbow | EA | 26
620016 | Project A | Area2 | Sub Area 21 | Section 212 | Tray | Al_Tray | AL | 6 | Fitting MTO | Field | Aluminum Ladder Tray | M | 200
620017 | Project A | Area2 | Sub Area 21 | Section 212 | Tray | 90Elbow | AL | 6 | Fitting MTO | Field | 90Elbow | EA | 10
620018 | Project A | Area2 | Sub Area 21 | Section 212 | Tray | 45Elbow | AL | 6 | Fitting MTO | Field | 45Elbow | EA | 10
620019 | Project A | Area3 | Sub Area 31 | Section 311 | Tray | Al_Tray | AL | 6 | Fitting MTO | Field | Aluminum Ladder Tray | M | 120
620020 | Project A | Area3 | Sub Area 31 | Section 311 | Tray | 90Elbow | AL | 6 | Fitting MTO | Field | 90Elbow | EA | 10
620021 | Project A | Area3 | Sub Area 31 | Section 311 | Tray | 45Elbow | AL | 6 | Fitting MTO | Field | 45Elbow | EA | 10
620022 | Project A | Area3 | Sub Area 31 | Section 312 | Tray | Al_Tray | AL | 30 | Fitting MTO | Field | Aluminum Ladder Tray | M | 10
620023 | Project A | Area3 | Sub Area 31 | Section 312 | Tray | Al_Tray | AL | 6 | Fitting MTO | Field | Aluminum Ladder Tray | M | 240
620024 | Project A | Area3 | Sub Area 31 | Section 312 | Tray | 90Elbow_Vertical | AL | 30 | Fitting MTO | Field | 90Elbow_Vertical | EA | 2
620025 | Project A | Area3 | Sub Area 31 | Section 312 | Tray | 90Elbow | AL | 30 | Fitting MTO | Field | 90Elbow | EA | 2
620026 | Project A | Area3 | Sub Area 31 | Section 312 | Tray | 90Elbow_Vertical | AL | 6 | Fitting MTO | Field | 90Elbow_Vertical | EA | 6
620027 | Project A | Area3 | Sub Area 31 | Section 312 | Tray | 90Elbow | AL | 6 | Fitting MTO | Field | 90Elbow | EA | 30
620028 | Project A | Area4 | Sub Area 41 | Section 411 | Tray | Al_Tray | AL | 12 | Fitting MTO | Field | Aluminum Ladder Tray | M | 600
620029 | Project A | Area4 | Sub Area 41 | Section 411 | Tray | 90Elbow_Vertical | AL | 12 | Fitting MTO | Field | 90Elbow_Vertical | EA | 6
620030 | Project A | Area4 | Sub Area 41 | Section 411 | Tray | 90Elbow | AL | 12 | Fitting MTO | Field | 90Elbow | EA | 10
620031 | Project A | Area4 | Sub Area 42 | Section 412 | Tray | Al_Tray | AL | 6 | Fitting MTO | Field | Aluminum Ladder Tray | M | 60
620032 | Project A | Area4 | Sub Area 42 | Section 412 | Tray | 90Elbow | AL | 6 | Fitting MTO | Field | 90Elbow | EA | 10
620033 | Project A | Area4 | Sub Area 42 | Section 412 | Tray | 45Elbow | AL | 6 | Fitting MTO | Field | 45Elbow | EA | 10
620034 | Project A | Area4 | Sub Area 43 | Section 413 | Tray | Al_Tray | AL | 6 | Fitting MTO | Field | Aluminum Ladder Tray | M | 300
620035 | Project A | Area4 | Sub Area 43 | Section 413 | Tray | 90Elbow_Vertical | AL | 6 | Fitting MTO | Field | 90Elbow_Vertical | EA | 10
620036 | Project A | Area4 | Sub Area 43 | Section 413 | Tray | 90Elbow | AL | 6 | Fitting MTO | Field | 90Elbow | EA | 30
620037 | Project A | Area4 | Sub Area 43 | Section 413 | Tray | Cross | AL | 6 | Fitting MTO | Field | Cross | EA | 4
620038 | Project A | Area4 | Sub Area 43 | Section 413 | Tray | Tee | AL | 6 | Fitting MTO | Field | Tee | EA | 3
Note: If fittings MTO is not available, a composite manhour basis can be applied to the tray quantities to allow for fittings
Electrical Bulks MTO Input Required - Cable Tray & Fittings
Example - Imaginary Project with made up quantities for Illustration Purposes
Go to Tab Index

## Conduit MTO Input
MTO_ID | WBS1 | WBS2 | WBS3 | WBS4 | CATEGORY | AG/Buried | Rigid Steel/ Electric Metal Tubing | Size (inch) | Fitting MTO or Composite | Module_Field | Description | Units | Quantity
630001 | Project A | Area1 | Sub Area 12 | Section 112 | Conduit | AG | RS | 2 | Composite | Field | Rigid Steel Conduit | M | 400
630002 | Project A | Area1 | Sub Area 12 | Section 112 | Conduit | AG | RS | 0.75 | Composite | Field | Rigid Steel Conduit | M | 500
Note: If fittings MTO is not available, a composite manhour basis can be applied to the conduit quantities to allow for fittings as it is in this case
Electrical Bulks MTO Input Required - Conduits & Fittings
Example - Imaginary Project with made up quantities for Illustration Purposes
Go to Tab Index

## Other Bulks MTO Input
MTO_ID | WBS1 | WBS2 | WBS3 | WBS4 | Category | Sub-Category | Size | Other specification as needed | Module_Field | Description | Units | Quantity
No MTO has been included for other electrical bulks in the example imaginary project; other items as needed are to be included in the MTOs here
Electrical Bulks MTO Input Required - Other Electrical Bulks
Example MTO Format - No quantities included in the example project
Go to Tab Index

## HazClass Input
WBS4 | Haz_Class
Section 111 | NonHaz
Section 112 | Haz
Section 211 | NonHaz
Section 221 | NonHaz
Section 311 | NonHaz
Section 312 | Haz
Section 411 | NonHaz
Section 412 | NonHaz
Section 413 | NonHaz
Area Classification Input Required
Example - Imaginary Project with made up Classifications for Illustration Purposes
Go to Tab Index

## LF & Wage Rate Input
Location | Location Factor* | Wage Rate
Module | 0.75 | 110
Field | 0.8 | 78
Productivity/Location Factor and Wage Rate Basis:
* Productivity/Location Factors used in this Example Imaginary Project reflect adjustment from typical US Gulf Coast Oil & Gas/Refinery projects based USGC Hours to the simple project with open access and single level rack and small contractor adjustment
* See page "Electrical Labor FAQs" on EstiResource website for project complexity and project size considerations in setting the productivity/location factor
Indicative Productivity/Location Factor for the project need to be provided by the project construction team, which can be refined during/after review of the first pass estimate
Wage Rate for Module Labor is to be provided by the project team as an all-inclusive rate (supervision, plant & equipment and overheads included) to be applied to the module craft labor hours as applicable in the proposed location for module contract
Wage Rate for Field Labor is to be provided by the project team based on the proposed execution strategy, either as all-in rate or as direct field labor rate if Indirect field costs and supervision will be included separately
Can provide different LF and Wage rate for different Areas if necessary
Electrical Bulks Productivity/Location Factor and Wage Rate Input Required
Example - Imaginary Project with made up basis for Illustration Purposes
Go to Tab Index

## Field Construction Plan
Field Construction | Book Ends for Planning |  |  |  | Calculated Finsh Date and Duration based on the Detail Planning
Construction Plan | Start | Finish | Duration (Days) | Total Field Hours | Start | Calculated Finish | Calculated Days | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9
Field | 2026-06-01 | 2026-09-29 | 120 | 7142 | 2026-06-01 | 2026-09-09 | 100
from the detail planning table below
Proposed Work-Week Cycle: 5 days x 10 hrs/day + 2 days off (50 hour work-week)
Effective hours per calendar day (adjusted for off days): =50/7 = 7.143 per worker
Field Construction Planning Basis
Field Construction Week Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Planned piping crew size | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Planned work hours/day | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Planned work-week cycle | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off
Work days/week | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Total crew hrs/calendar day | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286 | 71.4286
Use for planning purposes | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Choose different crew size and/or work week basis for any intermedite periods to allow for either pause of construction or reduced activity level due to seasonal weather or any other constraints; change the planned crew hours per calendar day in the detail planning to firm up the detail construction plan
Detail Construction Planning based on Estimated Field Hours by IWP
IWP Number | Estimated Hours | Planned crew hrs/Calendar Day | Work Days | Start | Finish | ROS (one week prior to start) | Construction Week No.
IWP-6001 | 530.5182 | 70 | 7.5788 | 2026-06-01 | 2026-06-09 | 2026-05-25 | 1
IWP-6002 | 166.4536 | 70 | 2.3779 | 2026-06-09 | 2026-06-11 | 2026-06-02 | 2
IWP-6003 | 173.4054 | 70 | 2.4772 | 2026-06-11 | 2026-06-13 | 2026-06-04 | 2
IWP-6004 | 130.9302 | 70 | 1.8704 | 2026-06-13 | 2026-06-15 | 2026-06-06 | 3
IWP-6005 | 270.3095 | 70 | 3.8616 | 2026-06-15 | 2026-06-19 | 2026-06-08 | 3
IWP-6006 | 55.6947 | 70 | 0.79564 | 2026-06-19 | 2026-06-20 | 2026-06-12 | 3
IWP-6007 | 151.5955 | 70 | 2.1657 | 2026-06-20 | 2026-06-22 | 2026-06-13 | 4
IWP-6008 | 179.0571 | 70 | 2.558 | 2026-06-22 | 2026-06-25 | 2026-06-15 | 4
IWP-6009 | 131.3078 | 70 | 1.8758 | 2026-06-25 | 2026-06-27 | 2026-06-18 | 4
IWP-6010 | 410.4284 | 70 | 5.8633 | 2026-06-27 | 2026-07-03 | 2026-06-20 | 5
IWP-6011 | 397.6383 | 70 | 5.6805 | 2026-07-03 | 2026-07-09 | 2026-06-26 | 6
IWP-6012 | 434.1117 | 70 | 6.2016 | 2026-07-09 | 2026-07-15 | 2026-07-02 | 7
IWP-6013 | 277.3185 | 70 | 3.9617 | 2026-07-15 | 2026-07-19 | 2026-07-08 | 7
IWP-6014 | 187.0957 | 70 | 2.6728 | 2026-07-19 | 2026-07-22 | 2026-07-12 | 8
IWP-6015 | 399.0359 | 70 | 5.7005 | 2026-07-22 | 2026-07-28 | 2026-07-15 | 9
IWP-6016 | 378.631 | 70 | 5.409 | 2026-07-28 | 2026-08-02 | 2026-07-21 | 9
IWP-6017 | 253.4512 | 70 | 3.6207 | 2026-08-02 | 2026-08-06 | 2026-07-26 | 10
IWP-6018 | 315.4165 | 70 | 4.5059 | 2026-08-06 | 2026-08-11 | 2026-07-30 | 11
IWP-6021 | 95.1473 | 70 | 1.3592 | 2026-08-11 | 2026-08-12 | 2026-08-04 | 11
IWP-6022 | 335.1046 | 70 | 4.7872 | 2026-08-12 | 2026-08-17 | 2026-08-05 | 12
IWP-6023 | 125.6748 | 70 | 1.7954 | 2026-08-17 | 2026-08-19 | 2026-08-10 | 12
IWP-6024 | 155.0456 | 70 | 2.2149 | 2026-08-19 | 2026-08-21 | 2026-08-12 | 12
IWP-6025 | 24.024 | 70 | 0.3432 | 2026-08-21 | 2026-08-21 | 2026-08-14 | 12
IWP-6026 | 124.464 | 70 | 1.7781 | 2026-08-21 | 2026-08-23 | 2026-08-14 | 12
IWP-6027 | 199.32 | 70 | 2.8474 | 2026-08-23 | 2026-08-26 | 2026-08-16 | 13
IWP-6028 | 262.6588 | 70 | 3.7523 | 2026-08-26 | 2026-08-30 | 2026-08-19 | 13
IWP-6029 | 321.5667 | 70 | 4.5938 | 2026-08-30 | 2026-09-04 | 2026-08-23 | 14
IWP-6030 | 188.6276 | 70 | 2.6947 | 2026-09-04 | 2026-09-07 | 2026-08-28 | 15
IWP-6031 | 127.8048 | 70 | 1.8258 | 2026-09-07 | 2026-09-09 | 2026-08-31 | 15
IWP-9999 | 340.0918 | 70 | 4.8585 | 2026-09-09 | 2026-09-09 | Various man-hr allowances
Total Field Hours | 7141.9291
Formulas:
Start = INT(Table2[[#This Row],[Total Field Hours]]+Table2[[#This Row],[Duration (Days)]]+0.5)
Start = Table2[[#This Row],[Total Field Hours]]
Finish = Table2[[#This Row],[Start]]+Table2[[#This Row],[Duration (Days)]]
Calculated Finish = Table2[[#This Row],[Total Field Hours]]-7
Total Field Hours = [Start, row above]
Field Construction Planning & Scheduling by Installation Work Package (IWP) - Input Required
Example - Imaginary Project with made up quantities for Illustration Purposes
Go to Tab Index

## Module Construction Plan
Module Construction | Book Ends for Planning |  |  |  | Calculated Finsh Date and Duration based on the Detail Planning
Construction Plan | Start | Finish | Duration (Days) | Total Module Hours | Start | Calculated Finish | Calculated Days | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9
Module | 2026-04-01 | 2026-05-11 | 40 | 1089 | 2026-04-01 | 2026-05-03 | 32
from the detail planning table below
Proposed Work-Week Cycle: 5 days x 10 hrs/day + 2 days off (50 hour work-week)
Effective hours per calendar day (adjusted for off days): =50/7 = 7.143 per worker
Module Construction Planning Basis
Module Construction Week Number | 1 | 2 | 3 | 4 | 5 | 6 | 7
Planned piping crew size | 5 | 5 | 5 | 5 | 5 | 5 | 5
Planned work hours/day | 10 | 10 | 10 | 10 | 10 | 10 | 10
Planned work-week cycle | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off | 5 days on 2 days off
Work days/week | 5 | 5 | 5 | 5 | 5 | 5 | 5
Total crew hrs/calendar day | 35.7143 | 35.7143 | 35.7143 | 35.7143 | 35.7143 | 35.7143 | 35.7143
Use for planning purposes | 30 | 30 | 30 | 30 | 30 | 30 | 30
Choose different crew size and/or work week basis as required; change the planned crew hours per calendar day in the detail planning to firm up the detail module construction plan
Detail Module Construction Planning based on Estimated Module Hours by IWP
IWP Number | Estimated Hours | Planned crew hrs/Calendar Day | Work Days | Start | Finish |  | Construction Week No.
IWP-6002 | 7.4635 | 30 | 0.24878 | 2026-04-01 | 2026-04-01 |  | 1
IWP-6003 | 5.9708 | 30 | 0.19903 | 2026-04-01 | 2026-04-01 |  | 1
IWP-6004 | 24.3049 | 30 | 0.81016 | 2026-04-01 | 2026-04-02 |  | 1
IWP-6005 | 24.8784 | 30 | 0.82928 | 2026-04-02 | 2026-04-03 |  | 1
IWP-6006 | 14.1238 | 30 | 0.47079 | 2026-04-03 | 2026-04-03 |  | 1
IWP-6007 | 7.4635 | 30 | 0.24878 | 2026-04-03 | 2026-04-03 |  | 1
IWP-6018 | 4.6453 | 30 | 0.15484 | 2026-04-03 | 2026-04-03 |  | 1
IWP-6019 | 208.899 | 30 | 6.9633 | 2026-04-03 | 2026-04-10 |  | 2
IWP-6020 | 97.7041 | 30 | 3.2568 | 2026-04-10 | 2026-04-13 |  | 2
IWP-6021 | 163.6096 | 30 | 5.4537 | 2026-04-13 | 2026-04-18 |  | 3
IWP-6022 | 27.3137 | 30 | 0.91046 | 2026-04-18 | 2026-04-19 |  | 3
IWP-6023 | 61.5 | 30 | 2.05 | 2026-04-19 | 2026-04-21 |  | 3
IWP-6024 | 11.0205 | 30 | 0.36735 | 2026-04-21 | 2026-04-21 |  | 3
IWP-6025 | 128.3835 | 30 | 4.2795 | 2026-04-21 | 2026-04-25 |  | 4
IWP-6026 | 72.3555 | 30 | 2.4118 | 2026-04-25 | 2026-04-27 |  | 4
IWP-6027 | 4.1655 | 30 | 0.13885 | 2026-04-27 | 2026-04-27 |  | 4
IWP-6028 | 22.625 | 30 | 0.75417 | 2026-04-27 | 2026-04-28 |  | 4
IWP-6029 | 23.8452 | 30 | 0.79484 | 2026-04-28 | 2026-04-29 |  | 5
IWP-6030 | 90.2442 | 30 | 3.0081 | 2026-04-29 | 2026-05-02 |  | 5
IWP-6031 | 40.551 | 30 | 1.3517 | 2026-05-02 | 2026-05-03 |  | 5
IWP-9999 | 47.4633 | 30 | 1.5821 | 2026-05-03 | 2026-05-03 | Various man-hr allowances
Total Module Hours | 1088.5304
Formulas:
Start = INT(Table26[[#This Row],[Total Module Hours]]+Table26[[#This Row],[Duration (Days)]]+0.5)
Start = Table26[[#This Row],[Total Module Hours]]
Finish = Table26[[#This Row],[Start]]+Table26[[#This Row],[Duration (Days)]]
Total Module Hours = [Start, row above]
Module Construction Planning & Scheduling by Installation Work Package (IWP) - Input Required
Example - Imaginary Project with made up quantities for Illustration Purposes
Go to Tab Index

## Allowances
CBS | Item Group | Location | Allowance % | Remarks
500 | 910 - Allowance for Miscellaneous Items | Module | 5% | of Module Labor hours
600 | 910 - Allowance for Miscellaneous Items | Field | 5% | of Field Labor hours
500 | Design development to IFC | Module | 0% | Client to determine; applied on grand total
600 | Design development to IFC | Field | 0% | Client to determine; applied on grand total
Allowances in Electrical Bulks Labor Estimate
Go to Tab Index

## Output-Labor Detail
MTO_ID | WBS1 | WBS2/Area | WBS3/Sub-Area | WBS4 | WBS_L/Cable No. | L1 | L2 | L2 Filter | L3 | Item_Group | L4 | L4 Filter | L5 | Size Group | CAT | SUB_CAT | Location | DESC | Units | Quantity | Runs | INSTALL | USGC | USGC_EXT | IWP | LF | Mod_Hrs | Field_Hrs | Wage Rate | Mod_$ | Field_$ | Total_ Hrs | Total_$
610001 | Project A | Area1 | Sub Area 11 | Section 111 | B-10001 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install DirBuried Cable6c14awg Cu 600V TECK, Direct Buried | M | 58 | 1 | DirBuried | 0.099424 | 5.7666 | IWP-6008 | 0.8 | 0 | 4.6133 | 78 | 0 | 359.8359 | 4.6133 | 359.8359
610001 | Project A | Area1 | Sub Area 11 | Section 111 | B-10001 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610001 | Project A | Area1 | Sub Area 11 | Section 111 | B-10001 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6021 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610002 | Project A | Area1 | Sub Area 11 | Section 111 | C-10002 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 55 | 1 | Tray | 0.095393 | 5.2466 | IWP-6008 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3903 | 4.1973 | 327.3903
610002 | Project A | Area1 | Sub Area 11 | Section 111 | C-10002 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610002 | Project A | Area1 | Sub Area 11 | Section 111 | C-10002 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610003 | Project A | Area1 | Sub Area 11 | Section 111 | C-10003 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 55 | 1 | Tray | 0.095393 | 5.2466 | IWP-6008 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3903 | 4.1973 | 327.3903
610003 | Project A | Area1 | Sub Area 11 | Section 111 | C-10003 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610003 | Project A | Area1 | Sub Area 11 | Section 111 | C-10003 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610004 | Project A | Area1 | Sub Area 11 | Section 111 | C-10004 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 92 | 1 | Tray | 0.095393 | 8.7762 | IWP-6008 | 0.8 | 0 | 7.021 | 78 | 0 | 547.6346 | 7.021 | 547.6346
610004 | Project A | Area1 | Sub Area 11 | Section 111 | C-10004 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610004 | Project A | Area1 | Sub Area 11 | Section 111 | C-10004 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610005 | Project A | Area1 | Sub Area 11 | Section 111 | C-10005 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 92 | 1 | Tray | 0.095393 | 8.7762 | IWP-6008 | 0.8 | 0 | 7.021 | 78 | 0 | 547.6346 | 7.021 | 547.6346
610005 | Project A | Area1 | Sub Area 11 | Section 111 | C-10005 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610005 | Project A | Area1 | Sub Area 11 | Section 111 | C-10005 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610006 | Project A | Area1 | Sub Area 11 | Section 111 | C-10006 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 55 | 1 | Tray | 0.095393 | 5.2466 | IWP-6008 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3903 | 4.1973 | 327.3903
610006 | Project A | Area1 | Sub Area 11 | Section 111 | C-10006 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610006 | Project A | Area1 | Sub Area 11 | Section 111 | C-10006 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610007 | Project A | Area1 | Sub Area 11 | Section 111 | C-10007 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 55 | 1 | Tray | 0.095393 | 5.2466 | IWP-6008 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3903 | 4.1973 | 327.3903
610007 | Project A | Area1 | Sub Area 11 | Section 111 | C-10007 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610007 | Project A | Area1 | Sub Area 11 | Section 111 | C-10007 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610008 | Project A | Area1 | Sub Area 11 | Section 111 | C-10008 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6008 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610008 | Project A | Area1 | Sub Area 11 | Section 111 | C-10008 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610008 | Project A | Area1 | Sub Area 11 | Section 111 | C-10008 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610009 | Project A | Area1 | Sub Area 11 | Section 111 | C-10009 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6008 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610009 | Project A | Area1 | Sub Area 11 | Section 111 | C-10009 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610009 | Project A | Area1 | Sub Area 11 | Section 111 | C-10009 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610010 | Project A | Area1 | Sub Area 11 | Section 111 | C-10010 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6008 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610010 | Project A | Area1 | Sub Area 11 | Section 111 | C-10010 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610010 | Project A | Area1 | Sub Area 11 | Section 111 | C-10010 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610011 | Project A | Area1 | Sub Area 11 | Section 111 | C-10011 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6008 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610011 | Project A | Area1 | Sub Area 11 | Section 111 | C-10011 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610011 | Project A | Area1 | Sub Area 11 | Section 111 | C-10011 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610012 | Project A | Area1 | Sub Area 11 | Section 111 | C-10012 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6008 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610012 | Project A | Area1 | Sub Area 11 | Section 111 | C-10012 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610012 | Project A | Area1 | Sub Area 11 | Section 111 | C-10012 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610013 | Project A | Area1 | Sub Area 11 | Section 111 | C-10013 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6008 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610013 | Project A | Area1 | Sub Area 11 | Section 111 | C-10013 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610013 | Project A | Area1 | Sub Area 11 | Section 111 | C-10013 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610014 | Project A | Area1 | Sub Area 11 | Section 111 | C-10014 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 5 | 1 | Tray | 0.095393 | 0.47697 | IWP-6008 | 0.8 | 0 | 0.38157 | 78 | 0 | 29.7628 | 0.38157 | 29.7628
610014 | Project A | Area1 | Sub Area 11 | Section 111 | C-10014 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610014 | Project A | Area1 | Sub Area 11 | Section 111 | C-10014 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610015 | Project A | Area1 | Sub Area 11 | Section 111 | C-10015 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 5 | 1 | Tray | 0.095393 | 0.47697 | IWP-6008 | 0.8 | 0 | 0.38157 | 78 | 0 | 29.7628 | 0.38157 | 29.7628
610015 | Project A | Area1 | Sub Area 11 | Section 111 | C-10015 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610015 | Project A | Area1 | Sub Area 11 | Section 111 | C-10015 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610016 | Project A | Area1 | Sub Area 11 | Section 111 | C-10016 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable12pr16awg Shld 300V ACIC, Random Fill | M | 5 | 1 | Tray | 0.21631 | 1.0816 | IWP-6019 | 0.75 | 0.81118 | 0 | 110 | 89.2298 | 0 | 0.81118 | 89.2298
610016 | Project A | Area1 | Sub Area 11 | Section 111 | C-10016 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6021 | 0.75 | 2.1937 | 0 | 110 | 241.3125 | 0 | 2.1937 | 241.3125
610016 | Project A | Area1 | Sub Area 11 | Section 111 | C-10016 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 48 | 1 |  | 0.132 | 6.336 | IWP-6021 | 0.75 | 4.752 | 0 | 110 | 522.72 | 0 | 4.752 | 522.72
610017 | Project A | Area1 | Sub Area 11 | Section 111 | C-10017 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.22572 | 1.1286 | IWP-6019 | 0.75 | 0.84645 | 0 | 110 | 93.1094 | 0 | 0.84645 | 93.1094
610017 | Project A | Area1 | Sub Area 11 | Section 111 | C-10017 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6021 | 0.75 | 2.1937 | 0 | 110 | 241.3125 | 0 | 2.1937 | 241.3125
610017 | Project A | Area1 | Sub Area 11 | Section 111 | C-10017 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6021 | 0.75 | 3.96 | 0 | 110 | 435.6 | 0 | 3.96 | 435.6
610018 | Project A | Area1 | Sub Area 11 | Section 111 | C-10018 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable12pr16awg Shld 300V ACIC, Random Fill | M | 5 | 1 | Tray | 0.21631 | 1.0816 | IWP-6019 | 0.75 | 0.81118 | 0 | 110 | 89.2298 | 0 | 0.81118 | 89.2298
610018 | Project A | Area1 | Sub Area 11 | Section 111 | C-10018 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6021 | 0.75 | 2.1937 | 0 | 110 | 241.3125 | 0 | 2.1937 | 241.3125
610018 | Project A | Area1 | Sub Area 11 | Section 111 | C-10018 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 48 | 1 |  | 0.132 | 6.336 | IWP-6021 | 0.75 | 4.752 | 0 | 110 | 522.72 | 0 | 4.752 | 522.72
610019 | Project A | Area1 | Sub Area 11 | Section 111 | C-10019 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.22572 | 1.1286 | IWP-6019 | 0.75 | 0.84645 | 0 | 110 | 93.1094 | 0 | 0.84645 | 93.1094
610019 | Project A | Area1 | Sub Area 11 | Section 111 | C-10019 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6021 | 0.75 | 2.1937 | 0 | 110 | 241.3125 | 0 | 2.1937 | 241.3125
610019 | Project A | Area1 | Sub Area 11 | Section 111 | C-10019 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6021 | 0.75 | 3.96 | 0 | 110 | 435.6 | 0 | 3.96 | 435.6
610020 | Project A | Area1 | Sub Area 11 | Section 111 | CAT-10001 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6019 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610020 | Project A | Area1 | Sub Area 11 | Section 111 | CAT-10001 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6021 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610020 | Project A | Area1 | Sub Area 11 | Section 111 | CAT-10001 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6021 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610021 | Project A | Area1 | Sub Area 11 | Section 111 | C-10020 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.23692 | 5.9229 | IWP-6019 | 0.75 | 4.4422 | 0 | 110 | 488.6395 | 0 | 4.4422 | 488.6395
610021 | Project A | Area1 | Sub Area 11 | Section 111 | C-10020 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6021 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610021 | Project A | Area1 | Sub Area 11 | Section 111 | C-10020 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6021 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610022 | Project A | Area1 | Sub Area 11 | Section 111 | C-10021 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.12988 | 1.2988 | IWP-6019 | 0.75 | 0.97409 | 0 | 110 | 107.1497 | 0 | 0.97409 | 107.1497
610022 | Project A | Area1 | Sub Area 11 | Section 111 | C-10021 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610022 | Project A | Area1 | Sub Area 11 | Section 111 | C-10021 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610023 | Project A | Area1 | Sub Area 11 | Section 111 | C-10022 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.12988 | 1.2988 | IWP-6019 | 0.75 | 0.97409 | 0 | 110 | 107.1497 | 0 | 0.97409 | 107.1497
610023 | Project A | Area1 | Sub Area 11 | Section 111 | C-10022 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610023 | Project A | Area1 | Sub Area 11 | Section 111 | C-10022 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610024 | Project A | Area1 | Sub Area 11 | Section 111 | C-10023 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.12988 | 1.2988 | IWP-6019 | 0.75 | 0.97409 | 0 | 110 | 107.1497 | 0 | 0.97409 | 107.1497
610024 | Project A | Area1 | Sub Area 11 | Section 111 | C-10023 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610024 | Project A | Area1 | Sub Area 11 | Section 111 | C-10023 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610025 | Project A | Area1 | Sub Area 11 | Section 111 | C-10024 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.10614 | 2.6536 | IWP-6008 | 0.8 | 0 | 2.1228 | 78 | 0 | 165.5815 | 2.1228 | 165.5815
610025 | Project A | Area1 | Sub Area 11 | Section 111 | C-10024 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610025 | Project A | Area1 | Sub Area 11 | Section 111 | C-10024 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610026 | Project A | Area1 | Sub Area 11 | Section 111 | C-10025 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 40 | 1 | Tray | 0.10614 | 4.2457 | IWP-6008 | 0.8 | 0 | 3.3965 | 78 | 0 | 264.9304 | 3.3965 | 264.9304
610026 | Project A | Area1 | Sub Area 11 | Section 111 | C-10025 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610026 | Project A | Area1 | Sub Area 11 | Section 111 | C-10025 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610027 | Project A | Area1 | Sub Area 11 | Section 111 | C-10026 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 90 | 1 | Tray | 0.10614 | 9.5528 | IWP-6008 | 0.8 | 0 | 7.6422 | 78 | 0 | 596.0935 | 7.6422 | 596.0935
610027 | Project A | Area1 | Sub Area 11 | Section 111 | C-10026 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610027 | Project A | Area1 | Sub Area 11 | Section 111 | C-10026 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610028 | Project A | Area1 | Sub Area 11 | Section 111 | C-10027 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.10614 | 1.0614 | IWP-6008 | 0.8 | 0 | 0.84914 | 78 | 0 | 66.2326 | 0.84914 | 66.2326
610028 | Project A | Area1 | Sub Area 11 | Section 111 | C-10027 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610028 | Project A | Area1 | Sub Area 11 | Section 111 | C-10027 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610029 | Project A | Area1 | Sub Area 11 | Section 111 | C-10028 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.10614 | 1.0614 | IWP-6008 | 0.8 | 0 | 0.84914 | 78 | 0 | 66.2326 | 0.84914 | 66.2326
610029 | Project A | Area1 | Sub Area 11 | Section 111 | C-10028 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610029 | Project A | Area1 | Sub Area 11 | Section 111 | C-10028 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610030 | Project A | Area1 | Sub Area 11 | Section 111 | C-10029 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 15 | 1 | Tray | 0.10614 | 1.5921 | IWP-6008 | 0.8 | 0 | 1.2737 | 78 | 0 | 99.3489 | 1.2737 | 99.3489
610030 | Project A | Area1 | Sub Area 11 | Section 111 | C-10029 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610030 | Project A | Area1 | Sub Area 11 | Section 111 | C-10029 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610031 | Project A | Area1 | Sub Area 11 | Section 111 | C-10030 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 15 | 1 | Tray | 0.10614 | 1.5921 | IWP-6008 | 0.8 | 0 | 1.2737 | 78 | 0 | 99.3489 | 1.2737 | 99.3489
610031 | Project A | Area1 | Sub Area 11 | Section 111 | C-10030 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610031 | Project A | Area1 | Sub Area 11 | Section 111 | C-10030 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6021 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610032 | Project A | Area1 | Sub Area 11 | Section 111 | C-10031 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6019 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610032 | Project A | Area1 | Sub Area 11 | Section 111 | C-10031 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610032 | Project A | Area1 | Sub Area 11 | Section 111 | C-10031 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610033 | Project A | Area1 | Sub Area 11 | Section 111 | C-10032 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6019 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610033 | Project A | Area1 | Sub Area 11 | Section 111 | C-10032 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610033 | Project A | Area1 | Sub Area 11 | Section 111 | C-10032 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610034 | Project A | Area1 | Sub Area 11 | Section 111 | C-10033 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6019 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610034 | Project A | Area1 | Sub Area 11 | Section 111 | C-10033 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6021 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610034 | Project A | Area1 | Sub Area 11 | Section 111 | C-10033 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610035 | Project A | Area1 | Sub Area 12 | Section 112 | C-10034 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1triad16awg Shld 300V ACIC, Random Fill | M | 31 | 1 | Tray | 0.10077 | 3.1238 | IWP-6008 | 0.8 | 0 | 2.499 | 78 | 0 | 194.925 | 2.499 | 194.925
610035 | Project A | Area1 | Sub Area 12 | Section 112 | C-10034 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610035 | Project A | Area1 | Sub Area 12 | Section 112 | C-10034 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.8 | 0 | 0.6336 | 78 | 0 | 49.4208 | 0.6336 | 49.4208
610036 | Project A | Area1 | Sub Area 12 | Section 112 | C-10035 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1triad16awg Shld 300V ACIC, Random Fill | M | 55 | 1 | Tray | 0.10077 | 5.5422 | IWP-6008 | 0.8 | 0 | 4.4338 | 78 | 0 | 345.8347 | 4.4338 | 345.8347
610036 | Project A | Area1 | Sub Area 12 | Section 112 | C-10035 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610036 | Project A | Area1 | Sub Area 12 | Section 112 | C-10035 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.8 | 0 | 0.6336 | 78 | 0 | 49.4208 | 0.6336 | 49.4208
610037 | Project A | Area1 | Sub Area 12 | Section 112 | C-10036 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1triad16awg Shld 300V ACIC, Random Fill | M | 80 | 1 | Tray | 0.10077 | 8.0614 | IWP-6008 | 0.8 | 0 | 6.4491 | 78 | 0 | 503.0324 | 6.4491 | 503.0324
610037 | Project A | Area1 | Sub Area 12 | Section 112 | C-10036 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610037 | Project A | Area1 | Sub Area 12 | Section 112 | C-10036 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.8 | 0 | 0.6336 | 78 | 0 | 49.4208 | 0.6336 | 49.4208
610038 | Project A | Area1 | Sub Area 12 | Section 112 | C-10037 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1triad16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.10077 | 1.0077 | IWP-6008 | 0.8 | 0 | 0.80614 | 78 | 0 | 62.879 | 0.80614 | 62.879
610038 | Project A | Area1 | Sub Area 12 | Section 112 | C-10037 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610038 | Project A | Area1 | Sub Area 12 | Section 112 | C-10037 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.8 | 0 | 0.6336 | 78 | 0 | 49.4208 | 0.6336 | 49.4208
610039 | Project A | Area1 | Sub Area 12 | Section 112 | C-10038 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1triad16awg Shld 300V ACIC, Random Fill | M | 15 | 1 | Tray | 0.10077 | 1.5115 | IWP-6008 | 0.8 | 0 | 1.2092 | 78 | 0 | 94.3186 | 1.2092 | 94.3186
610039 | Project A | Area1 | Sub Area 12 | Section 112 | C-10038 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610039 | Project A | Area1 | Sub Area 12 | Section 112 | C-10038 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.8 | 0 | 0.6336 | 78 | 0 | 49.4208 | 0.6336 | 49.4208
610040 | Project A | Area1 | Sub Area 12 | Section 112 | C-10039 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable14awg Cu, Random Fill | M | 5 | 1 | Tray | 0.17914 | 0.89571 | IWP-6019 | 0.75 | 0.67178 | 0 | 110 | 73.8963 | 0 | 0.67178 | 73.8963
610040 | Project A | Area1 | Sub Area 12 | Section 112 | C-10039 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610040 | Project A | Area1 | Sub Area 12 | Section 112 | C-10039 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 2 | 1 |  | 0.132 | 0.264 | IWP-6021 | 0.75 | 0.198 | 0 | 110 | 21.78 | 0 | 0.198 | 21.78
610041 | Project A | Area1 | Sub Area 12 | Section 112 | P-10003 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable1/0awg Cu 1kV TECK | M | 5 | 1 | Tray | 0.22001 | 1.1 | IWP-6019 | 0.75 | 0.82504 | 0 | 110 | 90.7539 | 0 | 0.82504 | 90.7539
610041 | Project A | Area1 | Sub Area 12 | Section 112 | P-10003 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 1.2 | 2.4 | IWP-6021 | 0.75 | 1.8 | 0 | 110 | 198 | 0 | 1.8 | 198
610041 | Project A | Area1 | Sub Area 12 | Section 112 | P-10003 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 2 | 1 |  | 0.429 | 0.858 | IWP-6021 | 0.75 | 0.6435 | 0 | 110 | 70.785 | 0 | 0.6435 | 70.785
610042 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10001 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6018 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610042 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10001 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610042 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10001 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610043 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10002 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6018 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610043 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10002 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610043 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10002 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610044 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10003 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6018 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610044 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10003 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610044 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10003 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610045 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10004 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6018 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610045 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10004 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610045 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10004 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610046 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10005 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6018 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610046 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10005 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610046 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10005 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610047 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10006 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6018 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610047 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10006 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610047 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10006 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610048 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10007 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6018 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610048 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10007 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610048 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10007 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610049 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10008 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6018 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610049 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10008 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610049 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10008 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610050 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10009 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610050 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10009 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610050 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10009 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610051 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10010 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610051 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10010 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610051 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10010 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610052 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10011 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610052 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10011 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610052 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10011 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610053 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10012 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610053 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10012 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610053 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10012 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610054 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10013 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610054 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10013 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610054 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10013 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610055 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10014 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6019 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610055 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10014 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610055 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10014 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610056 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10015 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6019 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610056 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10015 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610056 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10015 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610057 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10016 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610057 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10016 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610057 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10016 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610058 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10017 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6019 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610058 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10017 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610058 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10017 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610059 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10018 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610059 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10018 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610059 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10018 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610060 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10019 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610060 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10019 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610060 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10019 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610061 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10020 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610061 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10020 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610061 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10020 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610062 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10021 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610062 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10021 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610062 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10021 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610063 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10022 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610063 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10022 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610063 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10022 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610064 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10023 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610064 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10023 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610064 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10023 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610065 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10024 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6019 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610065 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10024 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610065 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10024 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610066 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10025 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6019 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610066 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10025 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610066 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10025 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610067 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10026 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610067 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10026 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610067 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10026 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610068 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10027 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610068 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10027 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610068 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10027 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610069 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10028 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610069 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10028 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610069 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10028 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610070 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10029 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610070 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10029 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610070 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10029 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610071 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10030 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610071 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10030 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610071 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10030 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610072 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10031 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610072 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10031 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610072 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10031 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610073 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10032 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610073 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10032 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610073 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10032 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610074 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10033 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610074 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10033 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610074 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10033 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610075 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10034 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610075 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10034 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610075 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10034 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610076 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10035 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610076 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10035 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610076 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10035 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610077 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10036 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610077 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10036 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610077 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10036 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610078 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10037 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610078 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10037 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610078 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10037 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610079 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10038 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610079 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10038 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610079 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10038 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610080 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10039 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6019 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610080 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10039 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610080 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10039 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610081 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10040 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6019 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610081 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10040 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610081 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10040 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610082 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10041 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610082 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10041 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610082 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10041 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610083 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10042 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6019 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610083 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10042 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610083 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10042 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610084 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10043 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610084 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10043 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610084 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10043 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610085 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10044 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610085 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10044 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610085 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10044 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610086 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10045 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6019 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610086 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10045 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6021 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610086 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10045 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610087 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10046 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610087 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10046 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610087 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10046 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610088 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10047 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610088 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10047 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610088 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10047 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610089 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10048 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610089 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10048 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610089 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10048 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610090 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10049 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6021 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610090 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10049 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610090 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10049 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610091 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10050 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6021 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610091 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10050 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610091 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10050 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610092 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10051 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610092 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10051 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610092 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10051 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610093 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10052 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610093 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10052 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610093 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10052 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610094 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10053 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610094 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10053 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610094 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10053 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610095 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10054 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610095 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10054 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610095 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10054 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610096 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10055 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610096 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10055 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610096 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10055 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610097 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10056 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610097 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10056 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610097 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10056 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610098 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10057 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610098 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10057 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610098 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10057 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610099 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10058 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610099 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10058 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610099 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10058 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610100 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10059 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610100 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10059 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610100 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10059 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610101 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10060 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610101 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10060 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610101 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10060 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610102 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10061 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610102 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10061 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610102 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10061 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610103 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10062 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610103 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10062 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610103 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10062 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610104 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10063 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610104 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10063 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610104 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10063 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610105 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10064 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6021 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610105 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10064 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610105 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10064 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610106 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10065 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6021 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610106 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10065 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610106 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10065 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610107 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10066 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610107 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10066 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610107 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10066 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610108 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10067 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6021 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610108 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10067 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610108 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10067 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610109 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10068 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610109 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10068 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610109 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10068 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610110 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10069 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610110 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10069 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610110 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10069 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610111 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10070 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610111 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10070 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610111 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10070 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610112 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10071 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610112 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10071 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610112 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10071 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610113 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10072 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610113 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10072 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610113 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10072 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610114 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10073 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.051615 | 0.77422 | IWP-6021 | 0.75 | 0.58066 | 0 | 110 | 63.873 | 0 | 0.58066 | 63.873
610114 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10073 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610114 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10073 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 6 | 1 |  | 0.132 | 0.792 | IWP-6021 | 0.75 | 0.594 | 0 | 110 | 65.34 | 0 | 0.594 | 65.34
610115 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10074 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6021 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610115 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10074 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610115 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10074 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610116 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10075 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Cond Cable16awg OS+TC 300V FEP, CMP | M | 15 | 1 | Cond | 0.050582 | 0.75873 | IWP-6021 | 0.75 | 0.56905 | 0 | 110 | 62.5956 | 0 | 0.56905 | 62.5956
610116 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10075 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6019 | 0.75 | 1.224 | 0 | 110 | 134.64 | 0 | 1.224 | 134.64
610116 | Project A | Area1 | Sub Area 12 | Section 112 | CO-10075 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6021 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610117 | Project A | Area1 | Sub Area 12 | Section 112 | FO-10001 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Fiber Optic | Field | Install Tray Cable Fiber-Optic 24 x SM, Armoured & Jacketed, Random Fill | M | 333 | 1 | Tray | 0.053743 | 17.8963 | IWP-6021 | 0.8 | 0 | 14.3171 | 78 | 0 | 1116.732 | 14.3171 | 1116.732
610117 | Project A | Area1 | Sub Area 12 | Section 112 | FO-10001 | 161 | 3 | 3 - Connectors | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16132709999 | 16132709999 - Connectors - Fiberoptic Cable | Connector | Fiber Optic | Field | Install Fiber Optic Connectors | EA | 2 | 1 |  | 2.08 | 4.16 | IWP-6008 | 0.8 | 0 | 3.328 | 78 | 0 | 259.584 | 3.328 | 259.584
610117 | Project A | Area1 | Sub Area 12 | Section 112 | FO-10001 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Fiber Optic | Field | Fiber Optic Terminations | EA | 48 | 1 |  | 0.52 | 24.96 | IWP-6008 | 0.8 | 0 | 19.968 | 78 | 0 | 1557.504 | 19.968 | 1557.504
610118 | Project A | Area1 | Sub Area 12 | Section 112 | C-10106 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 61 | 1 | Tray | 0.22572 | 13.7689 | IWP-6021 | 0.8 | 0 | 11.0151 | 78 | 0 | 859.1795 | 11.0151 | 859.1795
610118 | Project A | Area1 | Sub Area 12 | Section 112 | C-10106 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.8 | 3.6 | IWP-6008 | 0.8 | 0 | 2.88 | 78 | 0 | 224.64 | 2.88 | 224.64
610118 | Project A | Area1 | Sub Area 12 | Section 112 | C-10106 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6021 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610119 | Project A | Area1 | Sub Area 12 | Section 112 | C-10107 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 61 | 1 | Tray | 0.22572 | 13.7689 | IWP-6021 | 0.8 | 0 | 11.0151 | 78 | 0 | 859.1795 | 11.0151 | 859.1795
610119 | Project A | Area1 | Sub Area 12 | Section 112 | C-10107 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.8 | 3.6 | IWP-6008 | 0.8 | 0 | 2.88 | 78 | 0 | 224.64 | 2.88 | 224.64
610119 | Project A | Area1 | Sub Area 12 | Section 112 | C-10107 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6021 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610120 | Project A | Area1 | Sub Area 12 | Section 112 | C-10108 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 61 | 1 | Tray | 0.22572 | 13.7689 | IWP-6022 | 0.8 | 0 | 11.0151 | 78 | 0 | 859.1795 | 11.0151 | 859.1795
610120 | Project A | Area1 | Sub Area 12 | Section 112 | C-10108 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.8 | 3.6 | IWP-6008 | 0.8 | 0 | 2.88 | 78 | 0 | 224.64 | 2.88 | 224.64
610120 | Project A | Area1 | Sub Area 12 | Section 112 | C-10108 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6021 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610121 | Project A | Area1 | Sub Area 12 | Section 112 | C-10109 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 61 | 1 | Tray | 0.22572 | 13.7689 | IWP-6022 | 0.8 | 0 | 11.0151 | 78 | 0 | 859.1795 | 11.0151 | 859.1795
610121 | Project A | Area1 | Sub Area 12 | Section 112 | C-10109 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.8 | 3.6 | IWP-6008 | 0.8 | 0 | 2.88 | 78 | 0 | 224.64 | 2.88 | 224.64
610121 | Project A | Area1 | Sub Area 12 | Section 112 | C-10109 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6022 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610122 | Project A | Area1 | Sub Area 12 | Section 112 | C-10110 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 61 | 1 | Tray | 0.22572 | 13.7689 | IWP-6022 | 0.8 | 0 | 11.0151 | 78 | 0 | 859.1795 | 11.0151 | 859.1795
610122 | Project A | Area1 | Sub Area 12 | Section 112 | C-10110 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.8 | 3.6 | IWP-6008 | 0.8 | 0 | 2.88 | 78 | 0 | 224.64 | 2.88 | 224.64
610122 | Project A | Area1 | Sub Area 12 | Section 112 | C-10110 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6022 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610123 | Project A | Area2 | Sub Area 21 | Section 211 | C-10111 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 61 | 1 | Tray | 0.19079 | 11.638 | IWP-6022 | 0.8 | 0 | 9.3104 | 78 | 0 | 726.2113 | 9.3104 | 726.2113
610123 | Project A | Area2 | Sub Area 21 | Section 211 | C-10111 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6008 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610123 | Project A | Area2 | Sub Area 21 | Section 211 | C-10111 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6022 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610124 | Project A | Area2 | Sub Area 21 | Section 211 | C-10112 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6008 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610124 | Project A | Area2 | Sub Area 21 | Section 211 | C-10112 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 61 | 1 | Tray | 0.19079 | 11.638 | IWP-6022 | 0.8 | 0 | 9.3104 | 78 | 0 | 726.2113 | 9.3104 | 726.2113
610124 | Project A | Area2 | Sub Area 21 | Section 211 | C-10112 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6022 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610125 | Project A | Area2 | Sub Area 21 | Section 211 | C-10113 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610125 | Project A | Area2 | Sub Area 21 | Section 211 | C-10113 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 61 | 1 | Tray | 0.14331 | 8.7422 | IWP-6022 | 0.8 | 0 | 6.9937 | 78 | 0 | 545.5108 | 6.9937 | 545.5108
610125 | Project A | Area2 | Sub Area 21 | Section 211 | C-10113 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6022 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610126 | Project A | Area2 | Sub Area 21 | Section 211 | C-10114 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610126 | Project A | Area2 | Sub Area 21 | Section 211 | C-10114 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 61 | 1 | Tray | 0.1946 | 11.8708 | IWP-6022 | 0.8 | 0 | 9.4966 | 78 | 0 | 740.7353 | 9.4966 | 740.7353
610126 | Project A | Area2 | Sub Area 21 | Section 211 | C-10114 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6022 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610127 | Project A | Area2 | Sub Area 21 | Section 211 | C-10115 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610127 | Project A | Area2 | Sub Area 21 | Section 211 | C-10115 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 241 | 1 | Tray | 0.14331 | 34.5387 | IWP-6022 | 0.8 | 0 | 27.631 | 78 | 0 | 2155.2148 | 27.631 | 2155.2148
610127 | Project A | Area2 | Sub Area 21 | Section 211 | C-10115 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6022 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610128 | Project A | Area2 | Sub Area 21 | Section 211 | C-10116 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610128 | Project A | Area2 | Sub Area 21 | Section 211 | C-10116 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 100 | 1 | Tray | 0.12988 | 12.9878 | IWP-6022 | 0.8 | 0 | 10.3903 | 78 | 0 | 810.4412 | 10.3903 | 810.4412
610128 | Project A | Area2 | Sub Area 21 | Section 211 | C-10116 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610129 | Project A | Area2 | Sub Area 21 | Section 211 | P-10004 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6009 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610129 | Project A | Area2 | Sub Area 21 | Section 211 | P-10004 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 15 | 1 | Tray | 0.18228 | 2.7342 | IWP-6022 | 0.8 | 0 | 2.1873 | 78 | 0 | 170.6118 | 2.1873 | 170.6118
610129 | Project A | Area2 | Sub Area 21 | Section 211 | P-10004 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 4 | 1 |  | 0.26 | 1.04 | IWP-6022 | 0.8 | 0 | 0.832 | 78 | 0 | 64.896 | 0.832 | 64.896
610130 | Project A | Area2 | Sub Area 21 | Section 211 | C-10117 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610130 | Project A | Area2 | Sub Area 21 | Section 211 | C-10117 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.13257 | 3.3141 | IWP-6022 | 0.8 | 0 | 2.6513 | 78 | 0 | 206.8022 | 2.6513 | 206.8022
610130 | Project A | Area2 | Sub Area 21 | Section 211 | C-10117 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6022 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610131 | Project A | Area2 | Sub Area 21 | Section 211 | C-10118 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610131 | Project A | Area2 | Sub Area 21 | Section 211 | C-10118 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 47 | 1 | Tray | 0.13257 | 6.2306 | IWP-6022 | 0.8 | 0 | 4.9845 | 78 | 0 | 388.7881 | 4.9845 | 388.7881
610131 | Project A | Area2 | Sub Area 21 | Section 211 | C-10118 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6022 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610132 | Project A | Area2 | Sub Area 21 | Section 211 | C-10119 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6019 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610132 | Project A | Area2 | Sub Area 21 | Section 211 | C-10119 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.23692 | 1.1846 | IWP-6022 | 0.75 | 0.88844 | 0 | 110 | 97.7279 | 0 | 0.88844 | 97.7279
610132 | Project A | Area2 | Sub Area 21 | Section 211 | C-10119 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6022 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610133 | Project A | Area2 | Sub Area 21 | Section 211 | C-10120 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6019 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610133 | Project A | Area2 | Sub Area 21 | Section 211 | C-10120 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.23692 | 1.1846 | IWP-6022 | 0.75 | 0.88844 | 0 | 110 | 97.7279 | 0 | 0.88844 | 97.7279
610133 | Project A | Area2 | Sub Area 21 | Section 211 | C-10120 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6022 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610134 | Project A | Area2 | Sub Area 21 | Section 211 | C-10121 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6019 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610134 | Project A | Area2 | Sub Area 21 | Section 211 | C-10121 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.23692 | 1.1846 | IWP-6022 | 0.75 | 0.88844 | 0 | 110 | 97.7279 | 0 | 0.88844 | 97.7279
610134 | Project A | Area2 | Sub Area 21 | Section 211 | C-10121 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6022 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610135 | Project A | Area2 | Sub Area 21 | Section 211 | C-10122 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6019 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610135 | Project A | Area2 | Sub Area 21 | Section 211 | C-10122 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.23692 | 1.1846 | IWP-6022 | 0.75 | 0.88844 | 0 | 110 | 97.7279 | 0 | 0.88844 | 97.7279
610135 | Project A | Area2 | Sub Area 21 | Section 211 | C-10122 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6022 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610136 | Project A | Area2 | Sub Area 21 | Section 211 | C-10123 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610136 | Project A | Area2 | Sub Area 21 | Section 211 | C-10123 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 76 | 1 | Tray | 0.19079 | 14.4998 | IWP-6022 | 0.8 | 0 | 11.5998 | 78 | 0 | 904.7878 | 11.5998 | 904.7878
610136 | Project A | Area2 | Sub Area 21 | Section 211 | C-10123 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6022 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610137 | Project A | Area2 | Sub Area 21 | Section 211 | C-10124 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610137 | Project A | Area2 | Sub Area 21 | Section 211 | C-10124 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 76 | 1 | Tray | 0.19079 | 14.4998 | IWP-6022 | 0.8 | 0 | 11.5998 | 78 | 0 | 904.7878 | 11.5998 | 904.7878
610137 | Project A | Area2 | Sub Area 21 | Section 211 | C-10124 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6022 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610138 | Project A | Area2 | Sub Area 21 | Section 211 | C-10125 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610138 | Project A | Area2 | Sub Area 21 | Section 211 | C-10125 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 18 | 1 | Tray | 0.12988 | 2.3378 | IWP-6022 | 0.8 | 0 | 1.8702 | 78 | 0 | 145.8794 | 1.8702 | 145.8794
610138 | Project A | Area2 | Sub Area 21 | Section 211 | C-10125 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610139 | Project A | Area2 | Sub Area 21 | Section 211 | C-10126 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610139 | Project A | Area2 | Sub Area 21 | Section 211 | C-10126 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 13 | 1 | Tray | 0.12988 | 1.6884 | IWP-6022 | 0.8 | 0 | 1.3507 | 78 | 0 | 105.3574 | 1.3507 | 105.3574
610139 | Project A | Area2 | Sub Area 21 | Section 211 | C-10126 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610140 | Project A | Area2 | Sub Area 21 | Section 211 | C-10127 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610140 | Project A | Area2 | Sub Area 21 | Section 211 | C-10127 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.14331 | 3.5829 | IWP-6022 | 0.8 | 0 | 2.8663 | 78 | 0 | 223.57 | 2.8663 | 223.57
610140 | Project A | Area2 | Sub Area 21 | Section 211 | C-10127 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6022 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610141 | Project A | Area2 | Sub Area 21 | Section 211 | C-10128 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610141 | Project A | Area2 | Sub Area 21 | Section 211 | C-10128 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.10614 | 2.6536 | IWP-6022 | 0.8 | 0 | 2.1228 | 78 | 0 | 165.5815 | 2.1228 | 165.5815
610141 | Project A | Area2 | Sub Area 21 | Section 211 | C-10128 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610142 | Project A | Area2 | Sub Area 21 | Section 211 | C-10129 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610142 | Project A | Area2 | Sub Area 21 | Section 211 | C-10129 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.14331 | 3.5829 | IWP-6022 | 0.8 | 0 | 2.8663 | 78 | 0 | 223.57 | 2.8663 | 223.57
610142 | Project A | Area2 | Sub Area 21 | Section 211 | C-10129 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6022 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610143 | Project A | Area2 | Sub Area 21 | Section 211 | C-10130 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610143 | Project A | Area2 | Sub Area 21 | Section 211 | C-10130 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.10614 | 2.6536 | IWP-6022 | 0.8 | 0 | 2.1228 | 78 | 0 | 165.5815 | 2.1228 | 165.5815
610143 | Project A | Area2 | Sub Area 21 | Section 211 | C-10130 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610144 | Project A | Area2 | Sub Area 21 | Section 211 | C-10131 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610144 | Project A | Area2 | Sub Area 21 | Section 211 | C-10131 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 32 | 1 | Tray | 0.14331 | 4.5861 | IWP-6022 | 0.8 | 0 | 3.6688 | 78 | 0 | 286.1696 | 3.6688 | 286.1696
610144 | Project A | Area2 | Sub Area 21 | Section 211 | C-10131 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6022 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610145 | Project A | Area2 | Sub Area 21 | Section 211 | C-10132 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610145 | Project A | Area2 | Sub Area 21 | Section 211 | C-10132 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 32 | 1 | Tray | 0.10614 | 3.3965 | IWP-6022 | 0.8 | 0 | 2.7172 | 78 | 0 | 211.9443 | 2.7172 | 211.9443
610145 | Project A | Area2 | Sub Area 21 | Section 211 | C-10132 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610146 | Project A | Area2 | Sub Area 21 | Section 211 | C-10133 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610146 | Project A | Area2 | Sub Area 21 | Section 211 | C-10133 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 32 | 1 | Tray | 0.14331 | 4.5861 | IWP-6022 | 0.8 | 0 | 3.6688 | 78 | 0 | 286.1696 | 3.6688 | 286.1696
610146 | Project A | Area2 | Sub Area 21 | Section 211 | C-10133 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6022 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610147 | Project A | Area2 | Sub Area 21 | Section 211 | C-10134 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610147 | Project A | Area2 | Sub Area 21 | Section 211 | C-10134 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 32 | 1 | Tray | 0.10614 | 3.3965 | IWP-6022 | 0.8 | 0 | 2.7172 | 78 | 0 | 211.9443 | 2.7172 | 211.9443
610147 | Project A | Area2 | Sub Area 21 | Section 211 | C-10134 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610148 | Project A | Area2 | Sub Area 21 | Section 211 | P-10005 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable20c10awg Cu 600V CONDUIT, Random Fill | M | 10 | 1 | Tray | 0.27095 | 2.7095 | IWP-6022 | 0.8 | 0 | 2.1676 | 78 | 0 | 169.0748 | 2.1676 | 169.0748
610148 | Project A | Area2 | Sub Area 21 | Section 211 | P-10005 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6009 | 0.8 | 0 | 3.3072 | 78 | 0 | 257.9616 | 3.3072 | 257.9616
610148 | Project A | Area2 | Sub Area 21 | Section 211 | P-10005 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.176 | 7.04 | IWP-6022 | 0.8 | 0 | 5.632 | 78 | 0 | 439.296 | 5.632 | 439.296
610149 | Project A | Area2 | Sub Area 21 | Section 211 | C-10135 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12988 | 1.9482 | IWP-6022 | 0.8 | 0 | 1.5585 | 78 | 0 | 121.5662 | 1.5585 | 121.5662
610149 | Project A | Area2 | Sub Area 21 | Section 211 | C-10135 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610149 | Project A | Area2 | Sub Area 21 | Section 211 | C-10135 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610150 | Project A | Area2 | Sub Area 21 | Section 211 | C-10136 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 35 | 1 | Tray | 0.12988 | 4.5457 | IWP-6022 | 0.8 | 0 | 3.6366 | 78 | 0 | 283.6544 | 3.6366 | 283.6544
610150 | Project A | Area2 | Sub Area 21 | Section 211 | C-10136 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610150 | Project A | Area2 | Sub Area 21 | Section 211 | C-10136 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610151 | Project A | Area2 | Sub Area 21 | Section 211 | C-10137 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.12988 | 10.3903 | IWP-6022 | 0.8 | 0 | 8.3122 | 78 | 0 | 648.353 | 8.3122 | 648.353
610151 | Project A | Area2 | Sub Area 21 | Section 211 | C-10137 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610151 | Project A | Area2 | Sub Area 21 | Section 211 | C-10137 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610152 | Project A | Area2 | Sub Area 21 | Section 211 | C-10138 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 120 | 1 | Tray | 0.12988 | 15.5854 | IWP-6022 | 0.8 | 0 | 12.4683 | 78 | 0 | 972.5295 | 12.4683 | 972.5295
610152 | Project A | Area2 | Sub Area 21 | Section 211 | C-10138 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610152 | Project A | Area2 | Sub Area 21 | Section 211 | C-10138 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610153 | Project A | Area2 | Sub Area 21 | Section 211 | C-10139 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 95 | 1 | Tray | 0.12988 | 12.3384 | IWP-6022 | 0.8 | 0 | 9.8708 | 78 | 0 | 769.9192 | 9.8708 | 769.9192
610153 | Project A | Area2 | Sub Area 21 | Section 211 | C-10139 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610153 | Project A | Area2 | Sub Area 21 | Section 211 | C-10139 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610154 | Project A | Area2 | Sub Area 21 | Section 211 | C-10140 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.12988 | 10.3903 | IWP-6022 | 0.8 | 0 | 8.3122 | 78 | 0 | 648.353 | 8.3122 | 648.353
610154 | Project A | Area2 | Sub Area 21 | Section 211 | C-10140 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610154 | Project A | Area2 | Sub Area 21 | Section 211 | C-10140 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610155 | Project A | Area2 | Sub Area 21 | Section 211 | C-10141 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 70 | 1 | Tray | 0.12988 | 9.0915 | IWP-6022 | 0.8 | 0 | 7.2732 | 78 | 0 | 567.3089 | 7.2732 | 567.3089
610155 | Project A | Area2 | Sub Area 21 | Section 211 | C-10141 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610155 | Project A | Area2 | Sub Area 21 | Section 211 | C-10141 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610156 | Project A | Area2 | Sub Area 21 | Section 211 | C-10142 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 65 | 1 | Tray | 0.12988 | 8.4421 | IWP-6022 | 0.8 | 0 | 6.7537 | 78 | 0 | 526.7868 | 6.7537 | 526.7868
610156 | Project A | Area2 | Sub Area 21 | Section 211 | C-10142 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610156 | Project A | Area2 | Sub Area 21 | Section 211 | C-10142 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6022 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610157 | Project A | Area2 | Sub Area 21 | Section 211 | P-10006 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 30 | 1 | Tray | 0.14878 | 4.4633 | IWP-6022 | 0.8 | 0 | 3.5707 | 78 | 0 | 278.5122 | 3.5707 | 278.5122
610157 | Project A | Area2 | Sub Area 21 | Section 211 | P-10006 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610157 | Project A | Area2 | Sub Area 21 | Section 211 | P-10006 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6022 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610158 | Project A | Area2 | Sub Area 21 | Section 211 | C-10143 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable10c14awg Cu 600V TECK, Random Fill | M | 92 | 1 | Tray | 0.16929 | 15.5747 | IWP-6022 | 0.8 | 0 | 12.4597 | 78 | 0 | 971.8589 | 12.4597 | 971.8589
610158 | Project A | Area2 | Sub Area 21 | Section 211 | C-10143 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610158 | Project A | Area2 | Sub Area 21 | Section 211 | C-10143 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6022 | 0.8 | 0 | 2.112 | 78 | 0 | 164.736 | 2.112 | 164.736
610159 | Project A | Area2 | Sub Area 21 | Section 211 | P-10007 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 40 | 1 | Tray | 0.14878 | 5.9511 | IWP-6022 | 0.8 | 0 | 4.7609 | 78 | 0 | 371.3496 | 4.7609 | 371.3496
610159 | Project A | Area2 | Sub Area 21 | Section 211 | P-10007 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610159 | Project A | Area2 | Sub Area 21 | Section 211 | P-10007 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6022 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610160 | Project A | Area2 | Sub Area 21 | Section 211 | C-10144 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable10c14awg Cu 600V TECK, Random Fill | M | 126 | 1 | Tray | 0.16929 | 21.3305 | IWP-6022 | 0.8 | 0 | 17.0644 | 78 | 0 | 1331.0241 | 17.0644 | 1331.0241
610160 | Project A | Area2 | Sub Area 21 | Section 211 | C-10144 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610160 | Project A | Area2 | Sub Area 21 | Section 211 | C-10144 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6022 | 0.8 | 0 | 2.112 | 78 | 0 | 164.736 | 2.112 | 164.736
610161 | Project A | Area2 | Sub Area 21 | Section 211 | P-10008 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 55 | 1 | Tray | 0.14878 | 8.1828 | IWP-6022 | 0.8 | 0 | 6.5462 | 78 | 0 | 510.6058 | 6.5462 | 510.6058
610161 | Project A | Area2 | Sub Area 21 | Section 211 | P-10008 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610161 | Project A | Area2 | Sub Area 21 | Section 211 | P-10008 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6022 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610162 | Project A | Area2 | Sub Area 21 | Section 211 | C-10145 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable10c14awg Cu 600V TECK, Random Fill | M | 143 | 1 | Tray | 0.16929 | 24.2084 | IWP-6023 | 0.8 | 0 | 19.3668 | 78 | 0 | 1510.6067 | 19.3668 | 1510.6067
610162 | Project A | Area2 | Sub Area 21 | Section 211 | C-10145 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6009 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610162 | Project A | Area2 | Sub Area 21 | Section 211 | C-10145 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6022 | 0.8 | 0 | 2.112 | 78 | 0 | 164.736 | 2.112 | 164.736
610163 | Project A | Area2 | Sub Area 21 | Section 211 | C-10146 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 30 | 1 | Tray | 0.13257 | 3.977 | IWP-6023 | 0.8 | 0 | 3.1816 | 78 | 0 | 248.1626 | 3.1816 | 248.1626
610163 | Project A | Area2 | Sub Area 21 | Section 211 | C-10146 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610163 | Project A | Area2 | Sub Area 21 | Section 211 | C-10146 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6023 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610164 | Project A | Area2 | Sub Area 21 | Section 211 | C-10147 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 13 | 1 | Tray | 0.13257 | 1.7234 | IWP-6023 | 0.8 | 0 | 1.3787 | 78 | 0 | 107.5371 | 1.3787 | 107.5371
610164 | Project A | Area2 | Sub Area 21 | Section 211 | C-10147 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610164 | Project A | Area2 | Sub Area 21 | Section 211 | C-10147 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6023 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610165 | Project A | Area2 | Sub Area 21 | Section 211 | C-10148 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 30 | 1 | Tray | 0.13257 | 3.977 | IWP-6023 | 0.8 | 0 | 3.1816 | 78 | 0 | 248.1626 | 3.1816 | 248.1626
610165 | Project A | Area2 | Sub Area 21 | Section 211 | C-10148 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610165 | Project A | Area2 | Sub Area 21 | Section 211 | C-10148 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6023 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610166 | Project A | Area2 | Sub Area 21 | Section 211 | C-10149 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.13257 | 3.3141 | IWP-6023 | 0.8 | 0 | 2.6513 | 78 | 0 | 206.8022 | 2.6513 | 206.8022
610166 | Project A | Area2 | Sub Area 21 | Section 211 | C-10149 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6009 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610166 | Project A | Area2 | Sub Area 21 | Section 211 | C-10149 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6023 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610167 | Project A | Area2 | Sub Area 21 | Section 211 | P-10009 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 40 | 1 | Tray | 0.14878 | 5.9511 | IWP-6009 | 0.8 | 0 | 4.7609 | 78 | 0 | 371.3496 | 4.7609 | 371.3496
610167 | Project A | Area2 | Sub Area 21 | Section 211 | P-10009 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610167 | Project A | Area2 | Sub Area 21 | Section 211 | P-10009 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610168 | Project A | Area2 | Sub Area 21 | Section 211 | P-10010 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 40 | 1 | Tray | 0.14878 | 5.9511 | IWP-6009 | 0.8 | 0 | 4.7609 | 78 | 0 | 371.3496 | 4.7609 | 371.3496
610168 | Project A | Area2 | Sub Area 21 | Section 211 | P-10010 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610168 | Project A | Area2 | Sub Area 21 | Section 211 | P-10010 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610169 | Project A | Area2 | Sub Area 21 | Section 211 | P-10011 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 23 | 1 | Tray | 0.14878 | 3.4219 | IWP-6009 | 0.8 | 0 | 2.7375 | 78 | 0 | 213.526 | 2.7375 | 213.526
610169 | Project A | Area2 | Sub Area 21 | Section 211 | P-10011 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610169 | Project A | Area2 | Sub Area 21 | Section 211 | P-10011 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610170 | Project A | Area2 | Sub Area 21 | Section 211 | P-10012 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 60 | 1 | Tray | 0.14878 | 8.9267 | IWP-6009 | 0.8 | 0 | 7.1413 | 78 | 0 | 557.0245 | 7.1413 | 557.0245
610170 | Project A | Area2 | Sub Area 21 | Section 211 | P-10012 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610170 | Project A | Area2 | Sub Area 21 | Section 211 | P-10012 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610171 | Project A | Area2 | Sub Area 21 | Section 211 | P-10013 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 95 | 1 | Tray | 0.16257 | 15.4443 | IWP-6009 | 0.8 | 0 | 12.3555 | 78 | 0 | 963.7262 | 12.3555 | 963.7262
610171 | Project A | Area2 | Sub Area 21 | Section 211 | P-10013 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610171 | Project A | Area2 | Sub Area 21 | Section 211 | P-10013 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 4 | 1 |  | 0.198 | 0.792 | IWP-6023 | 0.8 | 0 | 0.6336 | 78 | 0 | 49.4208 | 0.6336 | 49.4208
610172 | Project A | Area2 | Sub Area 21 | Section 211 | P-10014 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 181 | 1 | Tray | 0.16257 | 29.4255 | IWP-6009 | 0.8 | 0 | 23.5404 | 78 | 0 | 1836.1521 | 23.5404 | 1836.1521
610172 | Project A | Area2 | Sub Area 21 | Section 211 | P-10014 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610172 | Project A | Area2 | Sub Area 21 | Section 211 | P-10014 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 4 | 1 |  | 0.198 | 0.792 | IWP-6023 | 0.8 | 0 | 0.6336 | 78 | 0 | 49.4208 | 0.6336 | 49.4208
610173 | Project A | Area2 | Sub Area 21 | Section 211 | P-10015 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.14878 | 3.7194 | IWP-6009 | 0.8 | 0 | 2.9756 | 78 | 0 | 232.0935 | 2.9756 | 232.0935
610173 | Project A | Area2 | Sub Area 21 | Section 211 | P-10015 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610173 | Project A | Area2 | Sub Area 21 | Section 211 | P-10015 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610174 | Project A | Area2 | Sub Area 21 | Section 211 | P-10016 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 195 | 1 | Tray | 0.14878 | 29.0117 | IWP-6009 | 0.8 | 0 | 23.2094 | 78 | 0 | 1810.3295 | 23.2094 | 1810.3295
610174 | Project A | Area2 | Sub Area 21 | Section 211 | P-10016 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610174 | Project A | Area2 | Sub Area 21 | Section 211 | P-10016 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610175 | Project A | Area2 | Sub Area 21 | Section 211 | C-10150 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable10c14awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.16929 | 1.6929 | IWP-6019 | 0.75 | 1.2697 | 0 | 110 | 139.6641 | 0 | 1.2697 | 139.6641
610175 | Project A | Area2 | Sub Area 21 | Section 211 | C-10150 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610175 | Project A | Area2 | Sub Area 21 | Section 211 | C-10150 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6023 | 0.75 | 1.98 | 0 | 110 | 217.8 | 0 | 1.98 | 217.8
610176 | Project A | Area2 | Sub Area 21 | Section 211 | P-10017 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable30c10awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.30454 | 1.5227 | IWP-6019 | 0.75 | 1.142 | 0 | 110 | 125.6237 | 0 | 1.142 | 125.6237
610176 | Project A | Area2 | Sub Area 21 | Section 211 | P-10017 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6023 | 0.75 | 4.212 | 0 | 110 | 463.32 | 0 | 4.212 | 463.32
610176 | Project A | Area2 | Sub Area 21 | Section 211 | P-10017 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.176 | 10.56 | IWP-6023 | 0.75 | 7.92 | 0 | 110 | 871.2 | 0 | 7.92 | 871.2
610177 | Project A | Area2 | Sub Area 21 | Section 211 | C-10151 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.13257 | 0.66283 | IWP-6019 | 0.75 | 0.49712 | 0 | 110 | 54.6833 | 0 | 0.49712 | 54.6833
610177 | Project A | Area2 | Sub Area 21 | Section 211 | C-10151 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610177 | Project A | Area2 | Sub Area 21 | Section 211 | C-10151 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6023 | 0.75 | 1.188 | 0 | 110 | 130.68 | 0 | 1.188 | 130.68
610178 | Project A | Area2 | Sub Area 21 | Section 211 | C-10152 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 17 | 1 | Tray | 0.13257 | 2.2536 | IWP-6019 | 0.75 | 1.6902 | 0 | 110 | 185.9231 | 0 | 1.6902 | 185.9231
610178 | Project A | Area2 | Sub Area 21 | Section 211 | C-10152 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610178 | Project A | Area2 | Sub Area 21 | Section 211 | C-10152 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6023 | 0.75 | 1.188 | 0 | 110 | 130.68 | 0 | 1.188 | 130.68
610179 | Project A | Area2 | Sub Area 21 | Section 211 | C-10153 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 17 | 1 | Tray | 0.13257 | 2.2536 | IWP-6019 | 0.75 | 1.6902 | 0 | 110 | 185.9231 | 0 | 1.6902 | 185.9231
610179 | Project A | Area2 | Sub Area 21 | Section 211 | C-10153 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610179 | Project A | Area2 | Sub Area 21 | Section 211 | C-10153 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6023 | 0.75 | 1.188 | 0 | 110 | 130.68 | 0 | 1.188 | 130.68
610180 | Project A | Area2 | Sub Area 21 | Section 211 | C-10154 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 11 | 1 | Tray | 0.13257 | 1.4582 | IWP-6019 | 0.75 | 1.0937 | 0 | 110 | 120.3032 | 0 | 1.0937 | 120.3032
610180 | Project A | Area2 | Sub Area 21 | Section 211 | C-10154 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610180 | Project A | Area2 | Sub Area 21 | Section 211 | C-10154 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6023 | 0.75 | 1.188 | 0 | 110 | 130.68 | 0 | 1.188 | 130.68
610181 | Project A | Area2 | Sub Area 21 | Section 211 | C-10155 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr14awg Shld 300v ACIC, Random Fill | M | 241 | 1 | Tray | 0.20033 | 48.2786 | IWP-6010 | 0.8 | 0 | 38.6229 | 78 | 0 | 3012.5855 | 38.6229 | 3012.5855
610181 | Project A | Area2 | Sub Area 21 | Section 211 | C-10155 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610181 | Project A | Area2 | Sub Area 21 | Section 211 | C-10155 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6023 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610182 | Project A | Area2 | Sub Area 21 | Section 211 | C-10156 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 241 | 1 | Tray | 0.19079 | 45.9796 | IWP-6010 | 0.8 | 0 | 36.7837 | 78 | 0 | 2869.1297 | 36.7837 | 2869.1297
610182 | Project A | Area2 | Sub Area 21 | Section 211 | C-10156 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610182 | Project A | Area2 | Sub Area 21 | Section 211 | C-10156 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6023 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610183 | Project A | Area2 | Sub Area 21 | Section 211 | C-10157 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 45 | 1 | Tray | 0.22572 | 10.1574 | IWP-6010 | 0.8 | 0 | 8.1259 | 78 | 0 | 633.8209 | 8.1259 | 633.8209
610183 | Project A | Area2 | Sub Area 21 | Section 211 | C-10157 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6023 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610183 | Project A | Area2 | Sub Area 21 | Section 211 | C-10157 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6023 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610184 | Project A | Area2 | Sub Area 21 | Section 211 | C-10158 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable6pr16awg Shld 300V ACIC, Random Fill | M | 45 | 1 | Tray | 0.16974 | 7.6382 | IWP-6010 | 0.8 | 0 | 6.1106 | 78 | 0 | 476.6232 | 6.1106 | 476.6232
610184 | Project A | Area2 | Sub Area 21 | Section 211 | C-10158 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610184 | Project A | Area2 | Sub Area 21 | Section 211 | C-10158 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6023 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610185 | Project A | Area2 | Sub Area 21 | Section 211 | P-10018 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 132 | 1 | Tray | 0.14878 | 19.6387 | IWP-6010 | 0.8 | 0 | 15.7109 | 78 | 0 | 1225.4538 | 15.7109 | 1225.4538
610185 | Project A | Area2 | Sub Area 21 | Section 211 | P-10018 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610185 | Project A | Area2 | Sub Area 21 | Section 211 | P-10018 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610186 | Project A | Area2 | Sub Area 21 | Section 211 | P-10019 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 5 | 1 | Tray | 0.13525 | 0.67626 | IWP-6010 | 0.8 | 0 | 0.54101 | 78 | 0 | 42.1988 | 0.54101 | 42.1988
610186 | Project A | Area2 | Sub Area 21 | Section 211 | P-10019 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610186 | Project A | Area2 | Sub Area 21 | Section 211 | P-10019 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6023 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610187 | Project A | Area2 | Sub Area 21 | Section 211 | P-10020 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg | M | 316 | 1 | Tray | 0.21452 | 67.7894 | IWP-6010 | 0.8 | 0 | 54.2315 | 78 | 0 | 4230.0562 | 54.2315 | 4230.0562
610187 | Project A | Area2 | Sub Area 21 | Section 211 | P-10020 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6023 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610187 | Project A | Area2 | Sub Area 21 | Section 211 | P-10020 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 8 | 1 |  | 0.26 | 2.08 | IWP-6023 | 0.8 | 0 | 1.664 | 78 | 0 | 129.792 | 1.664 | 129.792
610188 | Project A | Area2 | Sub Area 21 | Section 211 | P-10021 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 207 | 1 | Tray | 0.14878 | 30.797 | IWP-6010 | 0.8 | 0 | 24.6376 | 78 | 0 | 1921.7344 | 24.6376 | 1921.7344
610188 | Project A | Area2 | Sub Area 21 | Section 211 | P-10021 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610188 | Project A | Area2 | Sub Area 21 | Section 211 | P-10021 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610189 | Project A | Area2 | Sub Area 21 | Section 211 | P-10022 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 195 | 1 | Tray | 0.14878 | 29.0117 | IWP-6010 | 0.8 | 0 | 23.2094 | 78 | 0 | 1810.3295 | 23.2094 | 1810.3295
610189 | Project A | Area2 | Sub Area 21 | Section 211 | P-10022 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610189 | Project A | Area2 | Sub Area 21 | Section 211 | P-10022 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610190 | Project A | Area2 | Sub Area 21 | Section 211 | P-10023 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg | M | 316 | 1 | Tray | 0.21452 | 67.7894 | IWP-6010 | 0.8 | 0 | 54.2315 | 78 | 0 | 4230.0562 | 54.2315 | 4230.0562
610190 | Project A | Area2 | Sub Area 21 | Section 211 | P-10023 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6023 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610190 | Project A | Area2 | Sub Area 21 | Section 211 | P-10023 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 8 | 1 |  | 0.26 | 2.08 | IWP-6023 | 0.8 | 0 | 1.664 | 78 | 0 | 129.792 | 1.664 | 129.792
610191 | Project A | Area2 | Sub Area 21 | Section 211 | P-10024 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg | M | 149 | 1 | Tray | 0.21452 | 31.964 | IWP-6010 | 0.8 | 0 | 25.5712 | 78 | 0 | 1994.5518 | 25.5712 | 1994.5518
610191 | Project A | Area2 | Sub Area 21 | Section 211 | P-10024 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6023 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610191 | Project A | Area2 | Sub Area 21 | Section 211 | P-10024 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 8 | 1 |  | 0.26 | 2.08 | IWP-6023 | 0.8 | 0 | 1.664 | 78 | 0 | 129.792 | 1.664 | 129.792
610192 | Project A | Area2 | Sub Area 21 | Section 211 | P-10025 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 67 | 1 | Tray | 0.14878 | 9.9681 | IWP-6010 | 0.8 | 0 | 7.9745 | 78 | 0 | 622.0106 | 7.9745 | 622.0106
610192 | Project A | Area2 | Sub Area 21 | Section 211 | P-10025 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610192 | Project A | Area2 | Sub Area 21 | Section 211 | P-10025 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610193 | Project A | Area2 | Sub Area 21 | Section 211 | P-10026 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 67 | 1 | Tray | 0.14878 | 9.9681 | IWP-6010 | 0.8 | 0 | 7.9745 | 78 | 0 | 622.0106 | 7.9745 | 622.0106
610193 | Project A | Area2 | Sub Area 21 | Section 211 | P-10026 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610193 | Project A | Area2 | Sub Area 21 | Section 211 | P-10026 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610194 | Project A | Area2 | Sub Area 21 | Section 211 | P-10027 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 60 | 1 | Tray | 0.14878 | 8.9267 | IWP-6010 | 0.8 | 0 | 7.1413 | 78 | 0 | 557.0245 | 7.1413 | 557.0245
610194 | Project A | Area2 | Sub Area 21 | Section 211 | P-10027 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610194 | Project A | Area2 | Sub Area 21 | Section 211 | P-10027 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610195 | Project A | Area2 | Sub Area 21 | Section 211 | P-10028 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 5 | 1 | Tray | 0.12809 | 0.64044 | IWP-6019 | 0.75 | 0.48033 | 0 | 110 | 52.8359 | 0 | 0.48033 | 52.8359
610195 | Project A | Area2 | Sub Area 21 | Section 211 | P-10028 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610195 | Project A | Area2 | Sub Area 21 | Section 211 | P-10028 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610196 | Project A | Area2 | Sub Area 21 | Section 211 | P-10029 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 161 | 1 | Tray | 0.14878 | 23.9532 | IWP-6010 | 0.8 | 0 | 19.1626 | 78 | 0 | 1494.6823 | 19.1626 | 1494.6823
610196 | Project A | Area2 | Sub Area 21 | Section 211 | P-10029 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610196 | Project A | Area2 | Sub Area 21 | Section 211 | P-10029 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610197 | Project A | Area2 | Sub Area 21 | Section 211 | P-10030 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 50 | 1 | Tray | 0.14878 | 7.4389 | IWP-6010 | 0.8 | 0 | 5.9511 | 78 | 0 | 464.187 | 5.9511 | 464.187
610197 | Project A | Area2 | Sub Area 21 | Section 211 | P-10030 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610197 | Project A | Area2 | Sub Area 21 | Section 211 | P-10030 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610198 | Project A | Area2 | Sub Area 21 | Section 211 | P-10031 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 45 | 1 | Tray | 0.14878 | 6.695 | IWP-6010 | 0.8 | 0 | 5.356 | 78 | 0 | 417.7683 | 5.356 | 417.7683
610198 | Project A | Area2 | Sub Area 21 | Section 211 | P-10031 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610198 | Project A | Area2 | Sub Area 21 | Section 211 | P-10031 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610199 | Project A | Area2 | Sub Area 21 | Section 211 | P-10032 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 15 | 1 | Tray | 0.13525 | 2.0288 | IWP-6019 | 0.75 | 1.5216 | 0 | 110 | 167.3752 | 0 | 1.5216 | 167.3752
610199 | Project A | Area2 | Sub Area 21 | Section 211 | P-10032 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610199 | Project A | Area2 | Sub Area 21 | Section 211 | P-10032 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6023 | 0.75 | 0.7425 | 0 | 110 | 81.675 | 0 | 0.7425 | 81.675
610200 | Project A | Area2 | Sub Area 21 | Section 211 | P-10033 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 195 | 1 | Tray | 0.14878 | 29.0117 | IWP-6010 | 0.8 | 0 | 23.2094 | 78 | 0 | 1810.3295 | 23.2094 | 1810.3295
610200 | Project A | Area2 | Sub Area 21 | Section 211 | P-10033 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610200 | Project A | Area2 | Sub Area 21 | Section 211 | P-10033 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610201 | Project A | Area2 | Sub Area 21 | Section 211 | C-10159 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg, Unarmored | M | 11 | 1 | Tray | 0.095393 | 1.0493 | IWP-6010 | 0.8 | 0 | 0.83946 | 78 | 0 | 65.4781 | 0.83946 | 65.4781
610201 | Project A | Area2 | Sub Area 21 | Section 211 | C-10159 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.5304 | 1.0608 | IWP-6023 | 0.8 | 0 | 0.84864 | 78 | 0 | 66.1939 | 0.84864 | 66.1939
610201 | Project A | Area2 | Sub Area 21 | Section 211 | C-10159 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6023 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610202 | Project A | Area2 | Sub Area 21 | Section 211 | C-10160 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg, Unarmored | M | 13 | 1 | Tray | 0.095393 | 1.2401 | IWP-6010 | 0.8 | 0 | 0.99209 | 78 | 0 | 77.3832 | 0.99209 | 77.3832
610202 | Project A | Area2 | Sub Area 21 | Section 211 | C-10160 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.5304 | 1.0608 | IWP-6023 | 0.8 | 0 | 0.84864 | 78 | 0 | 66.1939 | 0.84864 | 66.1939
610202 | Project A | Area2 | Sub Area 21 | Section 211 | C-10160 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6023 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610203 | Project A | Area2 | Sub Area 21 | Section 211 | P-10034 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable6c10awg | M | 5 | 1 | Tray | 0.18362 | 0.91811 | IWP-6010 | 0.8 | 0 | 0.73448 | 78 | 0 | 57.2898 | 0.73448 | 57.2898
610203 | Project A | Area2 | Sub Area 21 | Section 211 | P-10034 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610203 | Project A | Area2 | Sub Area 21 | Section 211 | P-10034 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.176 | 2.112 | IWP-6023 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610204 | Project A | Area2 | Sub Area 21 | Section 211 | P-10035 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 132 | 1 | Tray | 0.14878 | 19.6387 | IWP-6010 | 0.8 | 0 | 15.7109 | 78 | 0 | 1225.4538 | 15.7109 | 1225.4538
610204 | Project A | Area2 | Sub Area 21 | Section 211 | P-10035 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610204 | Project A | Area2 | Sub Area 21 | Section 211 | P-10035 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610205 | Project A | Area2 | Sub Area 21 | Section 211 | P-10036 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable30c10awg | M | 60 | 1 | Tray | 0.30454 | 18.2725 | IWP-6010 | 0.8 | 0 | 14.618 | 78 | 0 | 1140.2067 | 14.618 | 1140.2067
610205 | Project A | Area2 | Sub Area 21 | Section 211 | P-10036 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6023 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610205 | Project A | Area2 | Sub Area 21 | Section 211 | P-10036 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 60 | 1 |  | 0.176 | 10.56 | IWP-6023 | 0.8 | 0 | 8.448 | 78 | 0 | 658.944 | 8.448 | 658.944
610206 | Project A | Area2 | Sub Area 21 | Section 211 | P-10037 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 10 | 1 | Tray | 0.12809 | 1.2809 | IWP-6019 | 0.75 | 0.96065 | 0 | 110 | 105.6718 | 0 | 0.96065 | 105.6718
610206 | Project A | Area2 | Sub Area 21 | Section 211 | P-10037 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610206 | Project A | Area2 | Sub Area 21 | Section 211 | P-10037 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610207 | Project A | Area2 | Sub Area 21 | Section 211 | P-10038 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 10 | 1 | Tray | 0.12809 | 1.2809 | IWP-6019 | 0.75 | 0.96065 | 0 | 110 | 105.6718 | 0 | 0.96065 | 105.6718
610207 | Project A | Area2 | Sub Area 21 | Section 211 | P-10038 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610207 | Project A | Area2 | Sub Area 21 | Section 211 | P-10038 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610208 | Project A | Area2 | Sub Area 21 | Section 211 | P-10039 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 5 | 1 | Tray | 0.12809 | 0.64044 | IWP-6019 | 0.75 | 0.48033 | 0 | 110 | 52.8359 | 0 | 0.48033 | 52.8359
610208 | Project A | Area2 | Sub Area 21 | Section 211 | P-10039 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610208 | Project A | Area2 | Sub Area 21 | Section 211 | P-10039 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610209 | Project A | Area2 | Sub Area 21 | Section 211 | P-10040 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 24 | 1 | Tray | 0.12809 | 3.0741 | IWP-6019 | 0.75 | 2.3056 | 0 | 110 | 253.6123 | 0 | 2.3056 | 253.6123
610209 | Project A | Area2 | Sub Area 21 | Section 211 | P-10040 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610209 | Project A | Area2 | Sub Area 21 | Section 211 | P-10040 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610210 | Project A | Area2 | Sub Area 21 | Section 211 | P-10041 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 10 | 1 | Tray | 0.12809 | 1.2809 | IWP-6019 | 0.75 | 0.96065 | 0 | 110 | 105.6718 | 0 | 0.96065 | 105.6718
610210 | Project A | Area2 | Sub Area 21 | Section 211 | P-10041 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610210 | Project A | Area2 | Sub Area 21 | Section 211 | P-10041 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610211 | Project A | Area2 | Sub Area 21 | Section 211 | P-10042 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 10 | 1 | Tray | 0.12809 | 1.2809 | IWP-6019 | 0.75 | 0.96065 | 0 | 110 | 105.6718 | 0 | 0.96065 | 105.6718
610211 | Project A | Area2 | Sub Area 21 | Section 211 | P-10042 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610211 | Project A | Area2 | Sub Area 21 | Section 211 | P-10042 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610212 | Project A | Area2 | Sub Area 21 | Section 211 | P-10043 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 14 | 1 | Tray | 0.12809 | 1.7932 | IWP-6019 | 0.75 | 1.3449 | 0 | 110 | 147.9405 | 0 | 1.3449 | 147.9405
610212 | Project A | Area2 | Sub Area 21 | Section 211 | P-10043 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610212 | Project A | Area2 | Sub Area 21 | Section 211 | P-10043 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610213 | Project A | Area2 | Sub Area 21 | Section 211 | P-10044 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 10 | 1 | Tray | 0.12809 | 1.2809 | IWP-6019 | 0.75 | 0.96065 | 0 | 110 | 105.6718 | 0 | 0.96065 | 105.6718
610213 | Project A | Area2 | Sub Area 21 | Section 211 | P-10044 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610213 | Project A | Area2 | Sub Area 21 | Section 211 | P-10044 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610214 | Project A | Area2 | Sub Area 21 | Section 211 | P-10045 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 5 | 1 | Tray | 0.12809 | 0.64044 | IWP-6019 | 0.75 | 0.48033 | 0 | 110 | 52.8359 | 0 | 0.48033 | 52.8359
610214 | Project A | Area2 | Sub Area 21 | Section 211 | P-10045 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610214 | Project A | Area2 | Sub Area 21 | Section 211 | P-10045 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6023 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610215 | Project A | Area2 | Sub Area 21 | Section 211 | P-10046 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable20c10awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.27095 | 1.3548 | IWP-6019 | 0.75 | 1.0161 | 0 | 110 | 111.7682 | 0 | 1.0161 | 111.7682
610215 | Project A | Area2 | Sub Area 21 | Section 211 | P-10046 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6023 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610215 | Project A | Area2 | Sub Area 21 | Section 211 | P-10046 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 40 | 1 |  | 0.176 | 7.04 | IWP-6023 | 0.75 | 5.28 | 0 | 110 | 580.8 | 0 | 5.28 | 580.8
610216 | Project A | Area2 | Sub Area 21 | Section 211 | P-10047 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.14878 | 1.4878 | IWP-6019 | 0.75 | 1.1158 | 0 | 110 | 122.7418 | 0 | 1.1158 | 122.7418
610216 | Project A | Area2 | Sub Area 21 | Section 211 | P-10047 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610216 | Project A | Area2 | Sub Area 21 | Section 211 | P-10047 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6023 | 0.75 | 0.528 | 0 | 110 | 58.08 | 0 | 0.528 | 58.08
610217 | Project A | Area2 | Sub Area 21 | Section 211 | P-10048 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable2awg Cu 1kV TECK, Random Fill | M | 5 | 1 | Tray | 0.18608 | 0.93042 | IWP-6019 | 0.75 | 0.69782 | 0 | 110 | 76.7598 | 0 | 0.69782 | 76.7598
610217 | Project A | Area2 | Sub Area 21 | Section 211 | P-10048 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610217 | Project A | Area2 | Sub Area 21 | Section 211 | P-10048 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 2 | 1 |  | 0.351 | 0.702 | IWP-6023 | 0.75 | 0.5265 | 0 | 110 | 57.915 | 0 | 0.5265 | 57.915
610218 | Project A | Area2 | Sub Area 21 | Section 211 | P-10049 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable6c10awg Cu 600V TECK, Random Fill | M | 18 | 1 | Tray | 0.18362 | 3.3052 | IWP-6019 | 0.75 | 2.4789 | 0 | 110 | 272.6775 | 0 | 2.4789 | 272.6775
610218 | Project A | Area2 | Sub Area 21 | Section 211 | P-10049 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610218 | Project A | Area2 | Sub Area 21 | Section 211 | P-10049 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.176 | 2.112 | IWP-6023 | 0.75 | 1.584 | 0 | 110 | 174.24 | 0 | 1.584 | 174.24
610219 | Project A | Area2 | Sub Area 21 | Section 211 | P-10050 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable6c10awg Cu 600V TECK, Random Fill | M | 20 | 1 | Tray | 0.18362 | 3.6724 | IWP-6019 | 0.75 | 2.7543 | 0 | 110 | 302.975 | 0 | 2.7543 | 302.975
610219 | Project A | Area2 | Sub Area 21 | Section 211 | P-10050 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610219 | Project A | Area2 | Sub Area 21 | Section 211 | P-10050 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.176 | 2.112 | IWP-6023 | 0.75 | 1.584 | 0 | 110 | 174.24 | 0 | 1.584 | 174.24
610220 | Project A | Area2 | Sub Area 21 | Section 211 | P-10051 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable6c10awg Cu 600V TECK, Random Fill | M | 22 | 1 | Tray | 0.18362 | 4.0397 | IWP-6019 | 0.75 | 3.0297 | 0 | 110 | 333.2725 | 0 | 3.0297 | 333.2725
610220 | Project A | Area2 | Sub Area 21 | Section 211 | P-10051 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6023 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610220 | Project A | Area2 | Sub Area 21 | Section 211 | P-10051 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.176 | 2.112 | IWP-6023 | 0.75 | 1.584 | 0 | 110 | 174.24 | 0 | 1.584 | 174.24
610221 | Project A | Area2 | Sub Area 21 | Section 211 | C-10161 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6010 | 0.8 | 0 | 2.5976 | 78 | 0 | 202.6103 | 2.5976 | 202.6103
610221 | Project A | Area2 | Sub Area 21 | Section 211 | C-10161 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610221 | Project A | Area2 | Sub Area 21 | Section 211 | C-10161 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6023 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610222 | Project A | Area2 | Sub Area 21 | Section 211 | C-10162 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6010 | 0.8 | 0 | 2.5976 | 78 | 0 | 202.6103 | 2.5976 | 202.6103
610222 | Project A | Area2 | Sub Area 21 | Section 211 | C-10162 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610222 | Project A | Area2 | Sub Area 21 | Section 211 | C-10162 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6023 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610223 | Project A | Area2 | Sub Area 21 | Section 211 | C-10163 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6010 | 0.8 | 0 | 2.5976 | 78 | 0 | 202.6103 | 2.5976 | 202.6103
610223 | Project A | Area2 | Sub Area 21 | Section 211 | C-10163 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6023 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610223 | Project A | Area2 | Sub Area 21 | Section 211 | C-10163 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6023 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610224 | Project A | Area2 | Sub Area 21 | Section 211 | C-10164 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6010 | 0.8 | 0 | 2.5976 | 78 | 0 | 202.6103 | 2.5976 | 202.6103
610224 | Project A | Area2 | Sub Area 21 | Section 211 | C-10164 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610224 | Project A | Area2 | Sub Area 21 | Section 211 | C-10164 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6024 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610225 | Project A | Area2 | Sub Area 21 | Section 211 | C-10165 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6010 | 0.8 | 0 | 2.5976 | 78 | 0 | 202.6103 | 2.5976 | 202.6103
610225 | Project A | Area2 | Sub Area 21 | Section 211 | C-10165 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610225 | Project A | Area2 | Sub Area 21 | Section 211 | C-10165 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6024 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610226 | Project A | Area2 | Sub Area 21 | Section 211 | C-10166 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6011 | 0.8 | 0 | 2.5976 | 78 | 0 | 202.6103 | 2.5976 | 202.6103
610226 | Project A | Area2 | Sub Area 21 | Section 211 | C-10166 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610226 | Project A | Area2 | Sub Area 21 | Section 211 | C-10166 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6024 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610227 | Project A | Area2 | Sub Area 21 | Section 211 | C-10167 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6011 | 0.8 | 0 | 2.5976 | 78 | 0 | 202.6103 | 2.5976 | 202.6103
610227 | Project A | Area2 | Sub Area 21 | Section 211 | C-10167 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610227 | Project A | Area2 | Sub Area 21 | Section 211 | C-10167 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6024 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610228 | Project A | Area2 | Sub Area 21 | Section 211 | C-10168 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 18 | 1 | Tray | 0.12988 | 2.3378 | IWP-6011 | 0.8 | 0 | 1.8702 | 78 | 0 | 145.8794 | 1.8702 | 145.8794
610228 | Project A | Area2 | Sub Area 21 | Section 211 | C-10168 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610228 | Project A | Area2 | Sub Area 21 | Section 211 | C-10168 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6024 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610229 | Project A | Area2 | Sub Area 21 | Section 211 | C-10169 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 13 | 1 | Tray | 0.12988 | 1.6884 | IWP-6011 | 0.8 | 0 | 1.3507 | 78 | 0 | 105.3574 | 1.3507 | 105.3574
610229 | Project A | Area2 | Sub Area 21 | Section 211 | C-10169 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610229 | Project A | Area2 | Sub Area 21 | Section 211 | C-10169 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6024 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610230 | Project A | Area2 | Sub Area 21 | Section 211 | C-10170 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 14 | 1 | Tray | 0.12988 | 1.8183 | IWP-6011 | 0.8 | 0 | 1.4546 | 78 | 0 | 113.4618 | 1.4546 | 113.4618
610230 | Project A | Area2 | Sub Area 21 | Section 211 | C-10170 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610230 | Project A | Area2 | Sub Area 21 | Section 211 | C-10170 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6024 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610231 | Project A | Area2 | Sub Area 21 | Section 211 | C-10171 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable40c14awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.24811 | 3.7217 | IWP-6019 | 0.75 | 2.7913 | 0 | 110 | 307.0392 | 0 | 2.7913 | 307.0392
610231 | Project A | Area2 | Sub Area 21 | Section 211 | C-10171 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6024 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610231 | Project A | Area2 | Sub Area 21 | Section 211 | C-10171 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 80 | 1 |  | 0.132 | 10.56 | IWP-6024 | 0.75 | 7.92 | 0 | 110 | 871.2 | 0 | 7.92 | 871.2
610232 | Project A | Area2 | Sub Area 21 | Section 211 | B-10002 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Field | Install DirBuried Cable4/0awg Cu 1kV TECK, Direct Buried | M | 20 | 1 | DirBuried | 0.26233 | 5.2466 | IWP-6008 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3902 | 4.1973 | 327.3902
610232 | Project A | Area2 | Sub Area 21 | Section 211 | B-10002 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6024 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610232 | Project A | Area2 | Sub Area 21 | Section 211 | B-10002 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.585 | 3.51 | IWP-6024 | 0.8 | 0 | 2.808 | 78 | 0 | 219.024 | 2.808 | 219.024
610233 | Project A | Area2 | Sub Area 21 | Section 211 | B-10003 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Field | Install DirBuried Cable4/0awg Cu 1kV TECK, Direct Buried | M | 20 | 1 | DirBuried | 0.26233 | 5.2466 | IWP-6008 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3902 | 4.1973 | 327.3902
610233 | Project A | Area2 | Sub Area 21 | Section 211 | B-10003 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6024 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610233 | Project A | Area2 | Sub Area 21 | Section 211 | B-10003 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.585 | 3.51 | IWP-6024 | 0.8 | 0 | 2.808 | 78 | 0 | 219.024 | 2.808 | 219.024
610234 | Project A | Area2 | Sub Area 21 | Section 211 | B-10004 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Field | Install DirBuried Cable4/0awg Cu 1kV TECK, Direct Buried | M | 20 | 1 | DirBuried | 0.26233 | 5.2466 | IWP-6008 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3902 | 4.1973 | 327.3902
610234 | Project A | Area2 | Sub Area 21 | Section 211 | B-10004 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6024 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610234 | Project A | Area2 | Sub Area 21 | Section 211 | B-10004 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.585 | 3.51 | IWP-6024 | 0.8 | 0 | 2.808 | 78 | 0 | 219.024 | 2.808 | 219.024
610235 | Project A | Area2 | Sub Area 21 | Section 211 | B-10005 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Field | Install DirBuried Cable4/0awg Cu 1kV TECK, Direct Buried | M | 20 | 1 | DirBuried | 0.26233 | 5.2466 | IWP-6008 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3902 | 4.1973 | 327.3902
610235 | Project A | Area2 | Sub Area 21 | Section 211 | B-10005 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6024 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610235 | Project A | Area2 | Sub Area 21 | Section 211 | B-10005 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.585 | 3.51 | IWP-6024 | 0.8 | 0 | 2.808 | 78 | 0 | 219.024 | 2.808 | 219.024
610236 | Project A | Area2 | Sub Area 21 | Section 211 | P-10056 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 50 | 1 | Tray | 0.14878 | 7.4389 | IWP-6011 | 0.8 | 0 | 5.9511 | 78 | 0 | 464.187 | 5.9511 | 464.187
610236 | Project A | Area2 | Sub Area 21 | Section 211 | P-10056 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610236 | Project A | Area2 | Sub Area 21 | Section 211 | P-10056 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6024 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610237 | Project A | Area2 | Sub Area 22 | Section 221 | C-10172 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg, Unarmored | M | 50 | 1 | Tray | 0.1946 | 9.7301 | IWP-6011 | 0.8 | 0 | 7.7841 | 78 | 0 | 607.1601 | 7.7841 | 607.1601
610237 | Project A | Area2 | Sub Area 22 | Section 221 | C-10172 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.78 | 1.56 | IWP-6024 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610237 | Project A | Area2 | Sub Area 22 | Section 221 | C-10172 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6024 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610238 | Project A | Area2 | Sub Area 22 | Section 221 | P-10057 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16122302002 | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Cable | 1kV | Field | Install Tray Cable500mcm | M | 50 | 1 | Tray | 0.47965 | 23.9827 | IWP-6011 | 0.8 | 0 | 19.1862 | 78 | 0 | 1496.5214 | 19.1862 | 1496.5214
610238 | Project A | Area2 | Sub Area 22 | Section 221 | P-10057 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16132302002 | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 3.666 | 7.332 | IWP-6024 | 0.8 | 0 | 5.8656 | 78 | 0 | 457.5168 | 5.8656 | 457.5168
610238 | Project A | Area2 | Sub Area 22 | Section 221 | P-10057 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16142302002 | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.91 | 5.46 | IWP-6024 | 0.8 | 0 | 4.368 | 78 | 0 | 340.704 | 4.368 | 340.704
610239 | Project A | Area2 | Sub Area 22 | Section 221 | P-10058 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 60 | 1 | Tray | 0.14878 | 8.9267 | IWP-6011 | 0.8 | 0 | 7.1413 | 78 | 0 | 557.0245 | 7.1413 | 557.0245
610239 | Project A | Area2 | Sub Area 22 | Section 221 | P-10058 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610239 | Project A | Area2 | Sub Area 22 | Section 221 | P-10058 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6024 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610240 | Project A | Area2 | Sub Area 22 | Section 221 | C-10173 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 60 | 1 | Tray | 0.1946 | 11.6762 | IWP-6011 | 0.8 | 0 | 9.3409 | 78 | 0 | 728.5921 | 9.3409 | 728.5921
610240 | Project A | Area2 | Sub Area 22 | Section 221 | C-10173 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6024 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610240 | Project A | Area2 | Sub Area 22 | Section 221 | C-10173 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6024 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610241 | Project A | Area2 | Sub Area 22 | Section 221 | P-10059 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16122302002 | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Cable | 1kV | Field | Install Tray Cable500mcm | M | 60 | 1 | Tray | 0.47965 | 28.7793 | IWP-6011 | 0.8 | 0 | 23.0234 | 78 | 0 | 1795.8257 | 23.0234 | 1795.8257
610241 | Project A | Area2 | Sub Area 22 | Section 221 | P-10059 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16132302002 | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 3.666 | 7.332 | IWP-6024 | 0.8 | 0 | 5.8656 | 78 | 0 | 457.5168 | 5.8656 | 457.5168
610241 | Project A | Area2 | Sub Area 22 | Section 221 | P-10059 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16142302002 | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.91 | 5.46 | IWP-6024 | 0.8 | 0 | 4.368 | 78 | 0 | 340.704 | 4.368 | 340.704
610242 | Project A | Area2 | Sub Area 22 | Section 221 | C-10174 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable10c14awg | M | 50 | 1 | Tray | 0.16929 | 8.4645 | IWP-6011 | 0.8 | 0 | 6.7716 | 78 | 0 | 528.1842 | 6.7716 | 528.1842
610242 | Project A | Area2 | Sub Area 22 | Section 221 | C-10174 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6024 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610242 | Project A | Area2 | Sub Area 22 | Section 221 | C-10174 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6024 | 0.8 | 0 | 2.112 | 78 | 0 | 164.736 | 2.112 | 164.736
610243 | Project A | Area2 | Sub Area 22 | Section 221 | C-10175 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable10c14awg | M | 60 | 1 | Tray | 0.16929 | 10.1574 | IWP-6011 | 0.8 | 0 | 8.1259 | 78 | 0 | 633.821 | 8.1259 | 633.821
610243 | Project A | Area2 | Sub Area 22 | Section 221 | C-10175 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6024 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610243 | Project A | Area2 | Sub Area 22 | Section 221 | C-10175 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6024 | 0.8 | 0 | 2.112 | 78 | 0 | 164.736 | 2.112 | 164.736
610244 | Project A | Area2 | Sub Area 22 | Section 221 | C-10176 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg | M | 316 | 1 | Tray | 0.18049 | 57.0336 | IWP-6011 | 0.8 | 0 | 45.6269 | 78 | 0 | 3558.8991 | 45.6269 | 3558.8991
610244 | Project A | Area2 | Sub Area 22 | Section 221 | C-10176 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6024 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610244 | Project A | Area2 | Sub Area 22 | Section 221 | C-10176 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6024 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610245 | Project A | Area2 | Sub Area 22 | Section 221 | P-10060 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 209 | 1 | Tray | 0.13525 | 28.2678 | IWP-6011 | 0.8 | 0 | 22.6143 | 78 | 0 | 1763.9116 | 22.6143 | 1763.9116
610245 | Project A | Area2 | Sub Area 22 | Section 221 | P-10060 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610245 | Project A | Area2 | Sub Area 22 | Section 221 | P-10060 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610246 | Project A | Area2 | Sub Area 22 | Section 221 | P-10061 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 207 | 1 | Tray | 0.13525 | 27.9973 | IWP-6011 | 0.8 | 0 | 22.3978 | 78 | 0 | 1747.0321 | 22.3978 | 1747.0321
610246 | Project A | Area2 | Sub Area 22 | Section 221 | P-10061 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610246 | Project A | Area2 | Sub Area 22 | Section 221 | P-10061 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610247 | Project A | Area2 | Sub Area 22 | Section 221 | P-10062 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 205 | 1 | Tray | 0.13525 | 27.7268 | IWP-6011 | 0.8 | 0 | 22.1814 | 78 | 0 | 1730.1525 | 22.1814 | 1730.1525
610247 | Project A | Area2 | Sub Area 22 | Section 221 | P-10062 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610247 | Project A | Area2 | Sub Area 22 | Section 221 | P-10062 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610248 | Project A | Area2 | Sub Area 22 | Section 221 | P-10063 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 120 | 1 | Tray | 0.13525 | 16.2303 | IWP-6011 | 0.8 | 0 | 12.9843 | 78 | 0 | 1012.7722 | 12.9843 | 1012.7722
610248 | Project A | Area2 | Sub Area 22 | Section 221 | P-10063 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610248 | Project A | Area2 | Sub Area 22 | Section 221 | P-10063 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610249 | Project A | Area2 | Sub Area 22 | Section 221 | P-10064 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 100 | 1 | Tray | 0.13525 | 13.5253 | IWP-6011 | 0.8 | 0 | 10.8202 | 78 | 0 | 843.9768 | 10.8202 | 843.9768
610249 | Project A | Area2 | Sub Area 22 | Section 221 | P-10064 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610249 | Project A | Area2 | Sub Area 22 | Section 221 | P-10064 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610250 | Project A | Area2 | Sub Area 22 | Section 221 | P-10065 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 120 | 1 | Tray | 0.13525 | 16.2303 | IWP-6011 | 0.8 | 0 | 12.9843 | 78 | 0 | 1012.7722 | 12.9843 | 1012.7722
610250 | Project A | Area2 | Sub Area 22 | Section 221 | P-10065 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610250 | Project A | Area2 | Sub Area 22 | Section 221 | P-10065 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610251 | Project A | Area2 | Sub Area 22 | Section 221 | P-10066 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 100 | 1 | Tray | 0.13525 | 13.5253 | IWP-6011 | 0.8 | 0 | 10.8202 | 78 | 0 | 843.9768 | 10.8202 | 843.9768
610251 | Project A | Area2 | Sub Area 22 | Section 221 | P-10066 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610251 | Project A | Area2 | Sub Area 22 | Section 221 | P-10066 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610252 | Project A | Area2 | Sub Area 22 | Section 221 | P-10067 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 126 | 1 | Tray | 0.13525 | 17.0418 | IWP-6011 | 0.8 | 0 | 13.6335 | 78 | 0 | 1063.4108 | 13.6335 | 1063.4108
610252 | Project A | Area2 | Sub Area 22 | Section 221 | P-10067 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610252 | Project A | Area2 | Sub Area 22 | Section 221 | P-10067 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610253 | Project A | Area2 | Sub Area 22 | Section 221 | P-10068 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 204 | 1 | Tray | 0.13525 | 27.5916 | IWP-6011 | 0.8 | 0 | 22.0732 | 78 | 0 | 1721.7128 | 22.0732 | 1721.7128
610253 | Project A | Area2 | Sub Area 22 | Section 221 | P-10068 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610253 | Project A | Area2 | Sub Area 22 | Section 221 | P-10068 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610254 | Project A | Area2 | Sub Area 22 | Section 221 | P-10069 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 207 | 1 | Tray | 0.13525 | 27.9973 | IWP-6011 | 0.8 | 0 | 22.3978 | 78 | 0 | 1747.0321 | 22.3978 | 1747.0321
610254 | Project A | Area2 | Sub Area 22 | Section 221 | P-10069 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610254 | Project A | Area2 | Sub Area 22 | Section 221 | P-10069 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610255 | Project A | Area2 | Sub Area 22 | Section 221 | P-10070 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 60 | 1 | Tray | 0.13525 | 8.1152 | IWP-6011 | 0.8 | 0 | 6.4921 | 78 | 0 | 506.3861 | 6.4921 | 506.3861
610255 | Project A | Area2 | Sub Area 22 | Section 221 | P-10070 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610255 | Project A | Area2 | Sub Area 22 | Section 221 | P-10070 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610256 | Project A | Area2 | Sub Area 22 | Section 221 | P-10071 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 55 | 1 | Tray | 0.13525 | 7.4389 | IWP-6011 | 0.8 | 0 | 5.9511 | 78 | 0 | 464.1873 | 5.9511 | 464.1873
610256 | Project A | Area2 | Sub Area 22 | Section 221 | P-10071 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610256 | Project A | Area2 | Sub Area 22 | Section 221 | P-10071 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610257 | Project A | Area2 | Sub Area 22 | Section 221 | P-10072 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 189 | 1 | Tray | 0.13525 | 25.5628 | IWP-6011 | 0.8 | 0 | 20.4502 | 78 | 0 | 1595.1162 | 20.4502 | 1595.1162
610257 | Project A | Area2 | Sub Area 22 | Section 221 | P-10072 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610257 | Project A | Area2 | Sub Area 22 | Section 221 | P-10072 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610258 | Project A | Area2 | Sub Area 22 | Section 221 | P-10073 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 195 | 1 | Tray | 0.13525 | 26.3743 | IWP-6011 | 0.8 | 0 | 21.0994 | 78 | 0 | 1645.7549 | 21.0994 | 1645.7549
610258 | Project A | Area2 | Sub Area 22 | Section 221 | P-10073 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610258 | Project A | Area2 | Sub Area 22 | Section 221 | P-10073 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610259 | Project A | Area2 | Sub Area 22 | Section 221 | P-10074 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 132 | 1 | Tray | 0.13525 | 17.8534 | IWP-6011 | 0.8 | 0 | 14.2827 | 78 | 0 | 1114.0494 | 14.2827 | 1114.0494
610259 | Project A | Area2 | Sub Area 22 | Section 221 | P-10074 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610259 | Project A | Area2 | Sub Area 22 | Section 221 | P-10074 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610260 | Project A | Area2 | Sub Area 22 | Section 221 | P-10075 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 126 | 1 | Tray | 0.13525 | 17.0418 | IWP-6011 | 0.8 | 0 | 13.6335 | 78 | 0 | 1063.4108 | 13.6335 | 1063.4108
610260 | Project A | Area2 | Sub Area 22 | Section 221 | P-10075 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610260 | Project A | Area2 | Sub Area 22 | Section 221 | P-10075 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610261 | Project A | Area2 | Sub Area 22 | Section 221 | P-10076 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 132 | 1 | Tray | 0.13525 | 17.8534 | IWP-6012 | 0.8 | 0 | 14.2827 | 78 | 0 | 1114.0494 | 14.2827 | 1114.0494
610261 | Project A | Area2 | Sub Area 22 | Section 221 | P-10076 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610261 | Project A | Area2 | Sub Area 22 | Section 221 | P-10076 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610262 | Project A | Area2 | Sub Area 22 | Section 221 | P-10077 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 126 | 1 | Tray | 0.13525 | 17.0418 | IWP-6012 | 0.8 | 0 | 13.6335 | 78 | 0 | 1063.4108 | 13.6335 | 1063.4108
610262 | Project A | Area2 | Sub Area 22 | Section 221 | P-10077 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610262 | Project A | Area2 | Sub Area 22 | Section 221 | P-10077 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610263 | Project A | Area2 | Sub Area 22 | Section 221 | P-10078 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 138 | 1 | Tray | 0.13525 | 18.6649 | IWP-6012 | 0.8 | 0 | 14.9319 | 78 | 0 | 1164.6881 | 14.9319 | 1164.6881
610263 | Project A | Area2 | Sub Area 22 | Section 221 | P-10078 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610263 | Project A | Area2 | Sub Area 22 | Section 221 | P-10078 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610264 | Project A | Area2 | Sub Area 22 | Section 221 | P-10079 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg | M | 316 | 1 | Tray | 0.13525 | 42.7399 | IWP-6012 | 0.8 | 0 | 34.1919 | 78 | 0 | 2666.9668 | 34.1919 | 2666.9668
610264 | Project A | Area2 | Sub Area 22 | Section 221 | P-10079 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6024 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610264 | Project A | Area2 | Sub Area 22 | Section 221 | P-10079 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6024 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610265 | Project A | Area2 | Sub Area 22 | Section 221 | C-10177 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg | M | 25 | 1 | Tray | 0.22572 | 5.643 | IWP-6012 | 0.8 | 0 | 4.5144 | 78 | 0 | 352.1227 | 4.5144 | 352.1227
610265 | Project A | Area2 | Sub Area 22 | Section 221 | C-10177 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6024 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610265 | Project A | Area2 | Sub Area 22 | Section 221 | C-10177 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6024 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610266 | Project A | Area2 | Sub Area 22 | Section 221 | P-10080 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable8awg | M | 316 | 1 | Tray | 0.18049 | 57.0336 | IWP-6012 | 0.8 | 0 | 45.6269 | 78 | 0 | 3558.8991 | 45.6269 | 3558.8991
610266 | Project A | Area2 | Sub Area 22 | Section 221 | P-10080 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6024 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610266 | Project A | Area2 | Sub Area 22 | Section 221 | P-10080 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6024 | 0.8 | 0 | 0.9504 | 78 | 0 | 74.1312 | 0.9504 | 74.1312
610267 | Project A | Area2 | Sub Area 22 | Section 221 | P-10081 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122202003 | 16122202003 - MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | Cable | 5kV | Field | Install Tray Cable1awg | M | 15 | 1 | Tray | 0.28215 | 4.2322 | IWP-6012 | 0.8 | 0 | 3.3858 | 78 | 0 | 264.092 | 3.3858 | 264.092
610267 | Project A | Area2 | Sub Area 22 | Section 221 | P-10081 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132202003 | 16132202003 - Connectors - MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6024 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610267 | Project A | Area2 | Sub Area 22 | Section 221 | P-10081 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142202003 | 16142202003 - Terminations - MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 3.575 | 21.45 | IWP-6024 | 0.8 | 0 | 17.16 | 78 | 0 | 1338.48 | 17.16 | 1338.48
610268 | Project A | Area2 | Sub Area 22 | Section 221 | P-10082 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Module | Install Tray Cable500mcm TECK | M | 20 | 1 | Tray | 0.53205 | 10.6411 | IWP-6019 | 0.75 | 7.9808 | 0 | 110 | 877.8883 | 0 | 7.9808 | 877.8883
610268 | Project A | Area2 | Sub Area 22 | Section 221 | P-10082 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Module | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6025 | 0.75 | 6.9615 | 0 | 110 | 765.765 | 0 | 6.9615 | 765.765
610268 | Project A | Area2 | Sub Area 22 | Section 221 | P-10082 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Module | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6025 | 0.75 | 29.25 | 0 | 110 | 3217.5 | 0 | 29.25 | 3217.5
610269 | Project A | Area2 | Sub Area 22 | Section 221 | P-10083 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Module | Install Tray Cable500mcm | M | 23 | 1 | Tray | 0.53205 | 12.2372 | IWP-6019 | 0.75 | 9.1779 | 0 | 110 | 1009.5715 | 0 | 9.1779 | 1009.5715
610269 | Project A | Area2 | Sub Area 22 | Section 221 | P-10083 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Module | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6025 | 0.75 | 6.9615 | 0 | 110 | 765.765 | 0 | 6.9615 | 765.765
610269 | Project A | Area2 | Sub Area 22 | Section 221 | P-10083 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Module | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6025 | 0.75 | 29.25 | 0 | 110 | 3217.5 | 0 | 29.25 | 3217.5
610270 | Project A | Area2 | Sub Area 22 | Section 221 | P-10084 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Module | Install Tray Cable500mcm | M | 23 | 1 | Tray | 0.53205 | 12.2372 | IWP-6019 | 0.75 | 9.1779 | 0 | 110 | 1009.5715 | 0 | 9.1779 | 1009.5715
610270 | Project A | Area2 | Sub Area 22 | Section 221 | P-10084 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Module | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6025 | 0.75 | 6.9615 | 0 | 110 | 765.765 | 0 | 6.9615 | 765.765
610270 | Project A | Area2 | Sub Area 22 | Section 221 | P-10084 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Module | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6025 | 0.75 | 29.25 | 0 | 110 | 3217.5 | 0 | 29.25 | 3217.5
610271 | Project A | Area2 | Sub Area 22 | Section 221 | P-10085 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable2awg | M | 22 | 1 | Tray | 0.24811 | 5.4585 | IWP-6019 | 0.75 | 4.0939 | 0 | 110 | 450.3242 | 0 | 4.0939 | 450.3242
610271 | Project A | Area2 | Sub Area 22 | Section 221 | P-10085 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6025 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610271 | Project A | Area2 | Sub Area 22 | Section 221 | P-10085 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.351 | 2.106 | IWP-6025 | 0.75 | 1.5795 | 0 | 110 | 173.745 | 0 | 1.5795 | 173.745
610272 | Project A | Area2 | Sub Area 22 | Section 221 | P-10086 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable2awg | M | 22 | 1 | Tray | 0.24811 | 5.4585 | IWP-6019 | 0.75 | 4.0939 | 0 | 110 | 450.3242 | 0 | 4.0939 | 450.3242
610272 | Project A | Area2 | Sub Area 22 | Section 221 | P-10086 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6025 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610272 | Project A | Area2 | Sub Area 22 | Section 221 | P-10086 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.351 | 2.106 | IWP-6025 | 0.75 | 1.5795 | 0 | 110 | 173.745 | 0 | 1.5795 | 173.745
610273 | Project A | Area2 | Sub Area 22 | Section 221 | P-10087 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 60 | 1 | Tray | 0.20333 | 12.1996 | IWP-6012 | 0.8 | 0 | 9.7597 | 78 | 0 | 761.2559 | 9.7597 | 761.2559
610273 | Project A | Area2 | Sub Area 22 | Section 221 | P-10087 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610273 | Project A | Area2 | Sub Area 22 | Section 221 | P-10087 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.26 | 1.56 | IWP-6025 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610274 | Project A | Area2 | Sub Area 22 | Section 221 | P-10088 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 75 | 1 | Tray | 0.20333 | 15.2495 | IWP-6012 | 0.8 | 0 | 12.1996 | 78 | 0 | 951.5699 | 12.1996 | 951.5699
610274 | Project A | Area2 | Sub Area 22 | Section 221 | P-10088 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610274 | Project A | Area2 | Sub Area 22 | Section 221 | P-10088 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.26 | 1.56 | IWP-6025 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610275 | Project A | Area2 | Sub Area 22 | Section 221 | P-10089 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 75 | 1 | Tray | 0.20333 | 15.2495 | IWP-6012 | 0.8 | 0 | 12.1996 | 78 | 0 | 951.5699 | 12.1996 | 951.5699
610275 | Project A | Area2 | Sub Area 22 | Section 221 | P-10089 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610275 | Project A | Area2 | Sub Area 22 | Section 221 | P-10089 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.26 | 1.56 | IWP-6025 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610276 | Project A | Area2 | Sub Area 22 | Section 221 | P-10090 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 85 | 1 | Tray | 0.20333 | 17.2828 | IWP-6012 | 0.8 | 0 | 13.8262 | 78 | 0 | 1078.4459 | 13.8262 | 1078.4459
610276 | Project A | Area2 | Sub Area 22 | Section 221 | P-10090 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610276 | Project A | Area2 | Sub Area 22 | Section 221 | P-10090 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.26 | 1.56 | IWP-6025 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610277 | Project A | Area2 | Sub Area 22 | Section 221 | P-10091 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 95 | 1 | Tray | 0.20333 | 19.3161 | IWP-6012 | 0.8 | 0 | 15.4528 | 78 | 0 | 1205.3219 | 15.4528 | 1205.3219
610277 | Project A | Area2 | Sub Area 22 | Section 221 | P-10091 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610277 | Project A | Area2 | Sub Area 22 | Section 221 | P-10091 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.26 | 1.56 | IWP-6025 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610278 | Project A | Area2 | Sub Area 22 | Section 221 | P-10092 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 126 | 1 | Tray | 0.20333 | 25.6192 | IWP-6012 | 0.8 | 0 | 20.4954 | 78 | 0 | 1598.6374 | 20.4954 | 1598.6374
610278 | Project A | Area2 | Sub Area 22 | Section 221 | P-10092 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610278 | Project A | Area2 | Sub Area 22 | Section 221 | P-10092 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.26 | 1.56 | IWP-6025 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610279 | Project A | Area2 | Sub Area 22 | Section 221 | P-10093 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 126 | 1 | Tray | 0.20333 | 25.6192 | IWP-6012 | 0.8 | 0 | 20.4954 | 78 | 0 | 1598.6374 | 20.4954 | 1598.6374
610279 | Project A | Area2 | Sub Area 22 | Section 221 | P-10093 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610279 | Project A | Area2 | Sub Area 22 | Section 221 | P-10093 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.26 | 1.56 | IWP-6025 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610280 | Project A | Area2 | Sub Area 22 | Section 221 | P-10094 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 143 | 1 | Tray | 0.20333 | 29.0757 | IWP-6012 | 0.8 | 0 | 23.2606 | 78 | 0 | 1814.3266 | 23.2606 | 1814.3266
610280 | Project A | Area2 | Sub Area 22 | Section 221 | P-10094 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610280 | Project A | Area2 | Sub Area 22 | Section 221 | P-10094 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.26 | 1.56 | IWP-6025 | 0.8 | 0 | 1.248 | 78 | 0 | 97.344 | 1.248 | 97.344
610281 | Project A | Area2 | Sub Area 22 | Section 221 | P-10095 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 20 | 1 | Tray | 0.18049 | 3.6097 | IWP-6019 | 0.75 | 2.7073 | 0 | 110 | 297.8022 | 0 | 2.7073 | 297.8022
610281 | Project A | Area2 | Sub Area 22 | Section 221 | P-10095 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610281 | Project A | Area2 | Sub Area 22 | Section 221 | P-10095 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6025 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610282 | Project A | Area2 | Sub Area 22 | Section 221 | P-10096 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 15 | 1 | Tray | 0.18049 | 2.7073 | IWP-6019 | 0.75 | 2.0305 | 0 | 110 | 223.3517 | 0 | 2.0305 | 223.3517
610282 | Project A | Area2 | Sub Area 22 | Section 221 | P-10096 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610282 | Project A | Area2 | Sub Area 22 | Section 221 | P-10096 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6025 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610283 | Project A | Area2 | Sub Area 22 | Section 221 | P-10097 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 15 | 1 | Tray | 0.18049 | 2.7073 | IWP-6019 | 0.75 | 2.0305 | 0 | 110 | 223.3517 | 0 | 2.0305 | 223.3517
610283 | Project A | Area2 | Sub Area 22 | Section 221 | P-10097 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610283 | Project A | Area2 | Sub Area 22 | Section 221 | P-10097 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6025 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610284 | Project A | Area2 | Sub Area 22 | Section 221 | P-10098 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 18 | 1 | Tray | 0.18049 | 3.2488 | IWP-6019 | 0.75 | 2.4366 | 0 | 110 | 268.022 | 0 | 2.4366 | 268.022
610284 | Project A | Area2 | Sub Area 22 | Section 221 | P-10098 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610284 | Project A | Area2 | Sub Area 22 | Section 221 | P-10098 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6025 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610285 | Project A | Area2 | Sub Area 22 | Section 221 | CAT-10002 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 15 | 1 | Tray | 0.03281 | 0.49215 | IWP-6019 | 0.75 | 0.36911 | 0 | 110 | 40.6024 | 0 | 0.36911 | 40.6024
610285 | Project A | Area2 | Sub Area 22 | Section 221 | CAT-10002 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6025 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610285 | Project A | Area2 | Sub Area 22 | Section 221 | CAT-10002 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6025 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610286 | Project A | Area2 | Sub Area 22 | Section 221 | C-10178 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 30 | 1 | Tray | 0.18049 | 5.4146 | IWP-6012 | 0.8 | 0 | 4.3317 | 78 | 0 | 337.8702 | 4.3317 | 337.8702
610286 | Project A | Area2 | Sub Area 22 | Section 221 | C-10178 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6025 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610286 | Project A | Area2 | Sub Area 22 | Section 221 | C-10178 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610287 | Project A | Area2 | Sub Area 22 | Section 221 | P-10100 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 20 | 1 | Tray | 0.18049 | 3.6097 | IWP-6019 | 0.75 | 2.7073 | 0 | 110 | 297.8022 | 0 | 2.7073 | 297.8022
610287 | Project A | Area2 | Sub Area 22 | Section 221 | P-10100 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610287 | Project A | Area2 | Sub Area 22 | Section 221 | P-10100 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6026 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610288 | Project A | Area2 | Sub Area 22 | Section 221 | P-10101 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 12 | 1 | Tray | 0.18049 | 2.1658 | IWP-6019 | 0.75 | 1.6244 | 0 | 110 | 178.6813 | 0 | 1.6244 | 178.6813
610288 | Project A | Area2 | Sub Area 22 | Section 221 | P-10101 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610288 | Project A | Area2 | Sub Area 22 | Section 221 | P-10101 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6026 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610289 | Project A | Area2 | Sub Area 22 | Section 221 | P-10102 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 10 | 1 | Tray | 0.18049 | 1.8049 | IWP-6019 | 0.75 | 1.3536 | 0 | 110 | 148.9011 | 0 | 1.3536 | 148.9011
610289 | Project A | Area2 | Sub Area 22 | Section 221 | P-10102 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610289 | Project A | Area2 | Sub Area 22 | Section 221 | P-10102 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6026 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610290 | Project A | Area2 | Sub Area 22 | Section 221 | P-10103 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 10 | 1 | Tray | 0.18049 | 1.8049 | IWP-6019 | 0.75 | 1.3536 | 0 | 110 | 148.9011 | 0 | 1.3536 | 148.9011
610290 | Project A | Area2 | Sub Area 22 | Section 221 | P-10103 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610290 | Project A | Area2 | Sub Area 22 | Section 221 | P-10103 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6026 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610291 | Project A | Area2 | Sub Area 22 | Section 221 | P-10104 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 100 | 1 | Tray | 0.15809 | 15.8093 | IWP-6012 | 0.8 | 0 | 12.6475 | 78 | 0 | 986.5022 | 12.6475 | 986.5022
610291 | Project A | Area2 | Sub Area 22 | Section 221 | P-10104 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610291 | Project A | Area2 | Sub Area 22 | Section 221 | P-10104 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6026 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610292 | Project A | Area2 | Sub Area 22 | Section 221 | P-10105 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 124 | 1 | Tray | 0.15809 | 19.6036 | IWP-6012 | 0.8 | 0 | 15.6829 | 78 | 0 | 1223.2627 | 15.6829 | 1223.2627
610292 | Project A | Area2 | Sub Area 22 | Section 221 | P-10105 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610292 | Project A | Area2 | Sub Area 22 | Section 221 | P-10105 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6026 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610293 | Project A | Area2 | Sub Area 22 | Section 221 | P-10106 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 128 | 1 | Tray | 0.15809 | 20.2359 | IWP-6012 | 0.8 | 0 | 16.1888 | 78 | 0 | 1262.7228 | 16.1888 | 1262.7228
610293 | Project A | Area2 | Sub Area 22 | Section 221 | P-10106 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610293 | Project A | Area2 | Sub Area 22 | Section 221 | P-10106 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6026 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610294 | Project A | Area2 | Sub Area 22 | Section 221 | P-10107 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 138 | 1 | Tray | 0.15809 | 21.8169 | IWP-6012 | 0.8 | 0 | 17.4535 | 78 | 0 | 1361.373 | 17.4535 | 1361.373
610294 | Project A | Area2 | Sub Area 22 | Section 221 | P-10107 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610294 | Project A | Area2 | Sub Area 22 | Section 221 | P-10107 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6026 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610295 | Project A | Area2 | Sub Area 22 | Section 221 | P-10108 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 142 | 1 | Tray | 0.15809 | 22.4492 | IWP-6012 | 0.8 | 0 | 17.9594 | 78 | 0 | 1400.8331 | 17.9594 | 1400.8331
610295 | Project A | Area2 | Sub Area 22 | Section 221 | P-10108 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610295 | Project A | Area2 | Sub Area 22 | Section 221 | P-10108 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6026 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610296 | Project A | Area2 | Sub Area 22 | Section 221 | P-10109 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 151 | 1 | Tray | 0.15809 | 23.8721 | IWP-6012 | 0.8 | 0 | 19.0977 | 78 | 0 | 1489.6183 | 19.0977 | 1489.6183
610296 | Project A | Area2 | Sub Area 22 | Section 221 | P-10109 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610296 | Project A | Area2 | Sub Area 22 | Section 221 | P-10109 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6026 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610297 | Project A | Area2 | Sub Area 22 | Section 221 | P-10110 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 43 | 1 | Tray | 0.13525 | 5.8159 | IWP-6012 | 0.8 | 0 | 4.6527 | 78 | 0 | 362.91 | 4.6527 | 362.91
610297 | Project A | Area2 | Sub Area 22 | Section 221 | P-10110 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610297 | Project A | Area2 | Sub Area 22 | Section 221 | P-10110 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610298 | Project A | Area2 | Sub Area 22 | Section 221 | C-10179 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 65 | 1 | Tray | 0.22572 | 14.6718 | IWP-6012 | 0.8 | 0 | 11.7374 | 78 | 0 | 915.5191 | 11.7374 | 915.5191
610298 | Project A | Area2 | Sub Area 22 | Section 221 | C-10179 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6026 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610298 | Project A | Area2 | Sub Area 22 | Section 221 | C-10179 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6026 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610299 | Project A | Area2 | Sub Area 22 | Section 221 | C-10180 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 65 | 1 | Tray | 0.22572 | 14.6718 | IWP-6012 | 0.8 | 0 | 11.7374 | 78 | 0 | 915.5191 | 11.7374 | 915.5191
610299 | Project A | Area2 | Sub Area 22 | Section 221 | C-10180 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6026 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610299 | Project A | Area2 | Sub Area 22 | Section 221 | C-10180 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6026 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610300 | Project A | Area2 | Sub Area 22 | Section 221 | C-10181 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 20 | 1 | Tray | 0.23692 | 4.7383 | IWP-6019 | 0.75 | 3.5537 | 0 | 110 | 390.9116 | 0 | 3.5537 | 390.9116
610300 | Project A | Area2 | Sub Area 22 | Section 221 | C-10181 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6026 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610300 | Project A | Area2 | Sub Area 22 | Section 221 | C-10181 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6026 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610301 | Project A | Area2 | Sub Area 22 | Section 221 | C-10182 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 20 | 1 | Tray | 0.23692 | 4.7383 | IWP-6019 | 0.75 | 3.5537 | 0 | 110 | 390.9116 | 0 | 3.5537 | 390.9116
610301 | Project A | Area2 | Sub Area 22 | Section 221 | C-10182 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6026 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610301 | Project A | Area2 | Sub Area 22 | Section 221 | C-10182 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6026 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610302 | Project A | Area2 | Sub Area 22 | Section 221 | C-10183 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 20 | 1 | Tray | 0.23692 | 4.7383 | IWP-6019 | 0.75 | 3.5537 | 0 | 110 | 390.9116 | 0 | 3.5537 | 390.9116
610302 | Project A | Area2 | Sub Area 22 | Section 221 | C-10183 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6026 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610302 | Project A | Area2 | Sub Area 22 | Section 221 | C-10183 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6026 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610303 | Project A | Area2 | Sub Area 22 | Section 221 | P-10111 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 30 | 1 | Tray | 0.18049 | 5.4146 | IWP-6012 | 0.8 | 0 | 4.3317 | 78 | 0 | 337.8702 | 4.3317 | 337.8702
610303 | Project A | Area2 | Sub Area 22 | Section 221 | P-10111 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610303 | Project A | Area2 | Sub Area 22 | Section 221 | P-10111 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6026 | 0.8 | 0 | 0.9504 | 78 | 0 | 74.1312 | 0.9504 | 74.1312
610304 | Project A | Area2 | Sub Area 22 | Section 221 | P-10112 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable4/0awg Cu 1kV TECK, Random Fill | M | 15 | 1 | Tray | 0.34978 | 5.2466 | IWP-6019 | 0.75 | 3.935 | 0 | 110 | 432.8477 | 0 | 3.935 | 432.8477
610304 | Project A | Area2 | Sub Area 22 | Section 221 | P-10112 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6026 | 0.75 | 4.212 | 0 | 110 | 463.32 | 0 | 4.212 | 463.32
610304 | Project A | Area2 | Sub Area 22 | Section 221 | P-10112 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.585 | 3.51 | IWP-6026 | 0.75 | 2.6325 | 0 | 110 | 289.575 | 0 | 2.6325 | 289.575
610305 | Project A | Area2 | Sub Area 22 | Section 221 | P-10113 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable4/0awg Cu 1kV TECK, Random Fill | M | 18 | 1 | Tray | 0.34978 | 6.296 | IWP-6019 | 0.75 | 4.722 | 0 | 110 | 519.4172 | 0 | 4.722 | 519.4172
610305 | Project A | Area2 | Sub Area 22 | Section 221 | P-10113 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6026 | 0.75 | 4.212 | 0 | 110 | 463.32 | 0 | 4.212 | 463.32
610305 | Project A | Area2 | Sub Area 22 | Section 221 | P-10113 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.585 | 3.51 | IWP-6026 | 0.75 | 2.6325 | 0 | 110 | 289.575 | 0 | 2.6325 | 289.575
610306 | Project A | Area2 | Sub Area 22 | Section 221 | P-10114 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Module | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 14 | 1 | Tray | 0.18049 | 2.5268 | IWP-6019 | 0.75 | 1.8951 | 0 | 110 | 208.4616 | 0 | 1.8951 | 208.4616
610306 | Project A | Area2 | Sub Area 22 | Section 221 | P-10114 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610306 | Project A | Area2 | Sub Area 22 | Section 221 | P-10114 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.198 | 1.188 | IWP-6026 | 0.75 | 0.891 | 0 | 110 | 98.01 | 0 | 0.891 | 98.01
610307 | Project A | Area2 | Sub Area 22 | Section 221 | P-10115 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.13525 | 0.67626 | IWP-6019 | 0.75 | 0.5072 | 0 | 110 | 55.7917 | 0 | 0.5072 | 55.7917
610307 | Project A | Area2 | Sub Area 22 | Section 221 | P-10115 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610307 | Project A | Area2 | Sub Area 22 | Section 221 | P-10115 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.75 | 0.7425 | 0 | 110 | 81.675 | 0 | 0.7425 | 81.675
610308 | Project A | Area2 | Sub Area 22 | Section 221 | P-10116 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable1awg Cu 1kV TECK, Random Fill | M | 5 | 1 | Tray | 0.27095 | 1.3548 | IWP-6019 | 0.75 | 1.0161 | 0 | 110 | 111.7682 | 0 | 1.0161 | 111.7682
610308 | Project A | Area2 | Sub Area 22 | Section 221 | P-10116 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6026 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610308 | Project A | Area2 | Sub Area 22 | Section 221 | P-10116 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.39 | 2.34 | IWP-6026 | 0.75 | 1.755 | 0 | 110 | 193.05 | 0 | 1.755 | 193.05
610309 | Project A | Area2 | Sub Area 22 | Section 221 | P-10117 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.13525 | 1.3525 | IWP-6019 | 0.75 | 1.0144 | 0 | 110 | 111.5835 | 0 | 1.0144 | 111.5835
610309 | Project A | Area2 | Sub Area 22 | Section 221 | P-10117 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610309 | Project A | Area2 | Sub Area 22 | Section 221 | P-10117 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.75 | 0.7425 | 0 | 110 | 81.675 | 0 | 0.7425 | 81.675
610310 | Project A | Area2 | Sub Area 22 | Section 221 | P-10118 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable1awg Cu 1kV TECK, Random Fill | M | 10 | 1 | Tray | 0.27095 | 2.7095 | IWP-6019 | 0.75 | 2.0321 | 0 | 110 | 223.5364 | 0 | 2.0321 | 223.5364
610310 | Project A | Area2 | Sub Area 22 | Section 221 | P-10118 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6026 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610310 | Project A | Area2 | Sub Area 22 | Section 221 | P-10118 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.39 | 2.34 | IWP-6026 | 0.75 | 1.755 | 0 | 110 | 193.05 | 0 | 1.755 | 193.05
610311 | Project A | Area2 | Sub Area 22 | Section 221 | P-10119 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.13525 | 1.3525 | IWP-6019 | 0.75 | 1.0144 | 0 | 110 | 111.5835 | 0 | 1.0144 | 111.5835
610311 | Project A | Area2 | Sub Area 22 | Section 221 | P-10119 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610311 | Project A | Area2 | Sub Area 22 | Section 221 | P-10119 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.75 | 0.7425 | 0 | 110 | 81.675 | 0 | 0.7425 | 81.675
610312 | Project A | Area2 | Sub Area 22 | Section 221 | P-10120 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable1awg Cu 1kV TECK, Random Fill | M | 10 | 1 | Tray | 0.27095 | 2.7095 | IWP-6019 | 0.75 | 2.0321 | 0 | 110 | 223.5364 | 0 | 2.0321 | 223.5364
610312 | Project A | Area2 | Sub Area 22 | Section 221 | P-10120 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6026 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610312 | Project A | Area2 | Sub Area 22 | Section 221 | P-10120 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.39 | 2.34 | IWP-6026 | 0.75 | 1.755 | 0 | 110 | 193.05 | 0 | 1.755 | 193.05
610313 | Project A | Area2 | Sub Area 22 | Section 221 | P-10121 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 65 | 1 | Tray | 0.13525 | 8.7914 | IWP-6012 | 0.8 | 0 | 7.0331 | 78 | 0 | 548.585 | 7.0331 | 548.585
610313 | Project A | Area2 | Sub Area 22 | Section 221 | P-10121 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610313 | Project A | Area2 | Sub Area 22 | Section 221 | P-10121 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610314 | Project A | Area2 | Sub Area 22 | Section 221 | P-10122 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 90 | 1 | Tray | 0.13525 | 12.1727 | IWP-6012 | 0.8 | 0 | 9.7382 | 78 | 0 | 759.5792 | 9.7382 | 759.5792
610314 | Project A | Area2 | Sub Area 22 | Section 221 | P-10122 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610314 | Project A | Area2 | Sub Area 22 | Section 221 | P-10122 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610315 | Project A | Area2 | Sub Area 22 | Section 221 | P-10123 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 95 | 1 | Tray | 0.13525 | 12.849 | IWP-6012 | 0.8 | 0 | 10.2792 | 78 | 0 | 801.778 | 10.2792 | 801.778
610315 | Project A | Area2 | Sub Area 22 | Section 221 | P-10123 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610315 | Project A | Area2 | Sub Area 22 | Section 221 | P-10123 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610316 | Project A | Area2 | Sub Area 22 | Section 221 | P-10124 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 120 | 1 | Tray | 0.13525 | 16.2303 | IWP-6012 | 0.8 | 0 | 12.9843 | 78 | 0 | 1012.7722 | 12.9843 | 1012.7722
610316 | Project A | Area2 | Sub Area 22 | Section 221 | P-10124 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610316 | Project A | Area2 | Sub Area 22 | Section 221 | P-10124 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610317 | Project A | Area2 | Sub Area 22 | Section 221 | P-10125 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 126 | 1 | Tray | 0.13525 | 17.0418 | IWP-6013 | 0.8 | 0 | 13.6335 | 78 | 0 | 1063.4108 | 13.6335 | 1063.4108
610317 | Project A | Area2 | Sub Area 22 | Section 221 | P-10125 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610317 | Project A | Area2 | Sub Area 22 | Section 221 | P-10125 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610318 | Project A | Area2 | Sub Area 22 | Section 221 | P-10126 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 138 | 1 | Tray | 0.13525 | 18.6649 | IWP-6013 | 0.8 | 0 | 14.9319 | 78 | 0 | 1164.6881 | 14.9319 | 1164.6881
610318 | Project A | Area2 | Sub Area 22 | Section 221 | P-10126 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6026 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610318 | Project A | Area2 | Sub Area 22 | Section 221 | P-10126 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.165 | 0.99 | IWP-6026 | 0.8 | 0 | 0.792 | 78 | 0 | 61.776 | 0.792 | 61.776
610319 | Project A | Area3 | Sub Area 31 | Section 311 | C-10184 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.18049 | 4.5122 | IWP-6013 | 0.8 | 0 | 3.6097 | 78 | 0 | 281.5585 | 3.6097 | 281.5585
610319 | Project A | Area3 | Sub Area 31 | Section 311 | C-10184 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610319 | Project A | Area3 | Sub Area 31 | Section 311 | C-10184 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610320 | Project A | Area3 | Sub Area 31 | Section 311 | C-10185 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 34 | 1 | Tray | 0.18049 | 6.1365 | IWP-6013 | 0.8 | 0 | 4.9092 | 78 | 0 | 382.9195 | 4.9092 | 382.9195
610320 | Project A | Area3 | Sub Area 31 | Section 311 | C-10185 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610320 | Project A | Area3 | Sub Area 31 | Section 311 | C-10185 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610321 | Project A | Area3 | Sub Area 31 | Section 311 | C-10186 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 28 | 1 | Tray | 0.18049 | 5.0536 | IWP-6013 | 0.8 | 0 | 4.0429 | 78 | 0 | 315.3455 | 4.0429 | 315.3455
610321 | Project A | Area3 | Sub Area 31 | Section 311 | C-10186 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610321 | Project A | Area3 | Sub Area 31 | Section 311 | C-10186 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610322 | Project A | Area3 | Sub Area 31 | Section 311 | C-10187 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 34 | 1 | Tray | 0.18049 | 6.1365 | IWP-6013 | 0.8 | 0 | 4.9092 | 78 | 0 | 382.9195 | 4.9092 | 382.9195
610322 | Project A | Area3 | Sub Area 31 | Section 311 | C-10187 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610322 | Project A | Area3 | Sub Area 31 | Section 311 | C-10187 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610323 | Project A | Area3 | Sub Area 31 | Section 311 | C-10188 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 33 | 1 | Tray | 0.18049 | 5.956 | IWP-6013 | 0.8 | 0 | 4.7648 | 78 | 0 | 371.6572 | 4.7648 | 371.6572
610323 | Project A | Area3 | Sub Area 31 | Section 311 | C-10188 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610323 | Project A | Area3 | Sub Area 31 | Section 311 | C-10188 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610324 | Project A | Area3 | Sub Area 31 | Section 311 | C-10189 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 33 | 1 | Tray | 0.18049 | 5.956 | IWP-6013 | 0.8 | 0 | 4.7648 | 78 | 0 | 371.6572 | 4.7648 | 371.6572
610324 | Project A | Area3 | Sub Area 31 | Section 311 | C-10189 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610324 | Project A | Area3 | Sub Area 31 | Section 311 | C-10189 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610325 | Project A | Area3 | Sub Area 31 | Section 311 | C-10190 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 33 | 1 | Tray | 0.18049 | 5.956 | IWP-6013 | 0.8 | 0 | 4.7648 | 78 | 0 | 371.6572 | 4.7648 | 371.6572
610325 | Project A | Area3 | Sub Area 31 | Section 311 | C-10190 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610325 | Project A | Area3 | Sub Area 31 | Section 311 | C-10190 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610326 | Project A | Area3 | Sub Area 31 | Section 311 | C-10191 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 33 | 1 | Tray | 0.18049 | 5.956 | IWP-6013 | 0.8 | 0 | 4.7648 | 78 | 0 | 371.6572 | 4.7648 | 371.6572
610326 | Project A | Area3 | Sub Area 31 | Section 311 | C-10191 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610326 | Project A | Area3 | Sub Area 31 | Section 311 | C-10191 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610327 | Project A | Area3 | Sub Area 31 | Section 311 | C-10192 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 43 | 1 | Tray | 0.18049 | 7.7609 | IWP-6013 | 0.8 | 0 | 6.2087 | 78 | 0 | 484.2806 | 6.2087 | 484.2806
610327 | Project A | Area3 | Sub Area 31 | Section 311 | C-10192 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610327 | Project A | Area3 | Sub Area 31 | Section 311 | C-10192 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610328 | Project A | Area3 | Sub Area 31 | Section 311 | C-10193 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 14 | 1 | Tray | 0.18049 | 2.5268 | IWP-6013 | 0.8 | 0 | 2.0214 | 78 | 0 | 157.6727 | 2.0214 | 157.6727
610328 | Project A | Area3 | Sub Area 31 | Section 311 | C-10193 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610328 | Project A | Area3 | Sub Area 31 | Section 311 | C-10193 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610329 | Project A | Area3 | Sub Area 31 | Section 311 | C-10194 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 16 | 1 | Tray | 0.18049 | 2.8878 | IWP-6013 | 0.8 | 0 | 2.3102 | 78 | 0 | 180.1974 | 2.3102 | 180.1974
610329 | Project A | Area3 | Sub Area 31 | Section 311 | C-10194 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610329 | Project A | Area3 | Sub Area 31 | Section 311 | C-10194 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610330 | Project A | Area3 | Sub Area 31 | Section 311 | C-10195 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 50 | 1 | Tray | 0.18049 | 9.0243 | IWP-6013 | 0.8 | 0 | 7.2194 | 78 | 0 | 563.1169 | 7.2194 | 563.1169
610330 | Project A | Area3 | Sub Area 31 | Section 311 | C-10195 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610330 | Project A | Area3 | Sub Area 31 | Section 311 | C-10195 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610331 | Project A | Area3 | Sub Area 31 | Section 311 | C-10196 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 53 | 1 | Tray | 0.18049 | 9.5658 | IWP-6013 | 0.8 | 0 | 7.6526 | 78 | 0 | 596.904 | 7.6526 | 596.904
610331 | Project A | Area3 | Sub Area 31 | Section 311 | C-10196 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610331 | Project A | Area3 | Sub Area 31 | Section 311 | C-10196 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610332 | Project A | Area3 | Sub Area 31 | Section 311 | C-10197 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.18049 | 4.5122 | IWP-6013 | 0.8 | 0 | 3.6097 | 78 | 0 | 281.5585 | 3.6097 | 281.5585
610332 | Project A | Area3 | Sub Area 31 | Section 311 | C-10197 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610332 | Project A | Area3 | Sub Area 31 | Section 311 | C-10197 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610333 | Project A | Area3 | Sub Area 31 | Section 311 | C-10198 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 29 | 1 | Tray | 0.18049 | 5.2341 | IWP-6013 | 0.8 | 0 | 4.1873 | 78 | 0 | 326.6078 | 4.1873 | 326.6078
610333 | Project A | Area3 | Sub Area 31 | Section 311 | C-10198 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610333 | Project A | Area3 | Sub Area 31 | Section 311 | C-10198 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610334 | Project A | Area3 | Sub Area 31 | Section 311 | C-10199 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 95 | 1 | Tray | 0.18049 | 17.1462 | IWP-6013 | 0.8 | 0 | 13.717 | 78 | 0 | 1069.9222 | 13.717 | 1069.9222
610334 | Project A | Area3 | Sub Area 31 | Section 311 | C-10199 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610334 | Project A | Area3 | Sub Area 31 | Section 311 | C-10199 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610335 | Project A | Area3 | Sub Area 31 | Section 311 | C-10200 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 95 | 1 | Tray | 0.18049 | 17.1462 | IWP-6013 | 0.8 | 0 | 13.717 | 78 | 0 | 1069.9222 | 13.717 | 1069.9222
610335 | Project A | Area3 | Sub Area 31 | Section 311 | C-10200 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610335 | Project A | Area3 | Sub Area 31 | Section 311 | C-10200 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610336 | Project A | Area3 | Sub Area 31 | Section 311 | C-10201 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 126 | 1 | Tray | 0.18049 | 22.7413 | IWP-6013 | 0.8 | 0 | 18.193 | 78 | 0 | 1419.0547 | 18.193 | 1419.0547
610336 | Project A | Area3 | Sub Area 31 | Section 311 | C-10201 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610336 | Project A | Area3 | Sub Area 31 | Section 311 | C-10201 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610337 | Project A | Area3 | Sub Area 31 | Section 311 | C-10202 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 126 | 1 | Tray | 0.18049 | 22.7413 | IWP-6013 | 0.8 | 0 | 18.193 | 78 | 0 | 1419.0547 | 18.193 | 1419.0547
610337 | Project A | Area3 | Sub Area 31 | Section 311 | C-10202 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610337 | Project A | Area3 | Sub Area 31 | Section 311 | C-10202 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610338 | Project A | Area3 | Sub Area 31 | Section 311 | C-10203 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 143 | 1 | Tray | 0.18049 | 25.8095 | IWP-6013 | 0.8 | 0 | 20.6476 | 78 | 0 | 1610.5145 | 20.6476 | 1610.5145
610338 | Project A | Area3 | Sub Area 31 | Section 311 | C-10203 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6026 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610338 | Project A | Area3 | Sub Area 31 | Section 311 | C-10203 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6026 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610339 | Project A | Area3 | Sub Area 31 | Section 311 | C-10204 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 143 | 1 | Tray | 0.18049 | 25.8095 | IWP-6013 | 0.8 | 0 | 20.6476 | 78 | 0 | 1610.5145 | 20.6476 | 1610.5145
610339 | Project A | Area3 | Sub Area 31 | Section 311 | C-10204 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610339 | Project A | Area3 | Sub Area 31 | Section 311 | C-10204 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610340 | Project A | Area3 | Sub Area 31 | Section 311 | C-10205 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 41 | 1 | Tray | 0.18049 | 7.3999 | IWP-6013 | 0.8 | 0 | 5.9199 | 78 | 0 | 461.7559 | 5.9199 | 461.7559
610340 | Project A | Area3 | Sub Area 31 | Section 311 | C-10205 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610340 | Project A | Area3 | Sub Area 31 | Section 311 | C-10205 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610341 | Project A | Area3 | Sub Area 31 | Section 311 | C-10206 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 41 | 1 | Tray | 0.18049 | 7.3999 | IWP-6013 | 0.8 | 0 | 5.9199 | 78 | 0 | 461.7559 | 5.9199 | 461.7559
610341 | Project A | Area3 | Sub Area 31 | Section 311 | C-10206 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610341 | Project A | Area3 | Sub Area 31 | Section 311 | C-10206 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610342 | Project A | Area3 | Sub Area 31 | Section 311 | C-10207 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 41 | 1 | Tray | 0.18049 | 7.3999 | IWP-6013 | 0.8 | 0 | 5.9199 | 78 | 0 | 461.7559 | 5.9199 | 461.7559
610342 | Project A | Area3 | Sub Area 31 | Section 311 | C-10207 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610342 | Project A | Area3 | Sub Area 31 | Section 311 | C-10207 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610343 | Project A | Area3 | Sub Area 31 | Section 311 | C-10208 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 41 | 1 | Tray | 0.18049 | 7.3999 | IWP-6013 | 0.8 | 0 | 5.9199 | 78 | 0 | 461.7559 | 5.9199 | 461.7559
610343 | Project A | Area3 | Sub Area 31 | Section 311 | C-10208 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610343 | Project A | Area3 | Sub Area 31 | Section 311 | C-10208 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610344 | Project A | Area3 | Sub Area 31 | Section 311 | C-10209 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 48 | 1 | Tray | 0.18049 | 8.6633 | IWP-6013 | 0.8 | 0 | 6.9307 | 78 | 0 | 540.5923 | 6.9307 | 540.5923
610344 | Project A | Area3 | Sub Area 31 | Section 311 | C-10209 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610344 | Project A | Area3 | Sub Area 31 | Section 311 | C-10209 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610345 | Project A | Area3 | Sub Area 31 | Section 311 | C-10210 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 11 | 1 | Tray | 0.18049 | 1.9853 | IWP-6013 | 0.8 | 0 | 1.5883 | 78 | 0 | 123.8857 | 1.5883 | 123.8857
610345 | Project A | Area3 | Sub Area 31 | Section 311 | C-10210 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610345 | Project A | Area3 | Sub Area 31 | Section 311 | C-10210 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610346 | Project A | Area3 | Sub Area 31 | Section 311 | C-10211 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable114awg Cu 600V TECK, Random Fill | M | 13 | 1 | Tray | 0.18049 | 2.3463 | IWP-6013 | 0.8 | 0 | 1.8771 | 78 | 0 | 146.4104 | 1.8771 | 146.4104
610346 | Project A | Area3 | Sub Area 31 | Section 311 | C-10211 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610346 | Project A | Area3 | Sub Area 31 | Section 311 | C-10211 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610347 | Project A | Area3 | Sub Area 31 | Section 311 | C-10212 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable6awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.10166 | 2.5416 | IWP-6013 | 0.8 | 0 | 2.0333 | 78 | 0 | 158.5949 | 2.0333 | 158.5949
610347 | Project A | Area3 | Sub Area 31 | Section 311 | C-10212 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6027 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610347 | Project A | Area3 | Sub Area 31 | Section 311 | C-10212 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 2 | 1 |  | 0.26 | 0.52 | IWP-6027 | 0.8 | 0 | 0.416 | 78 | 0 | 32.448 | 0.416 | 32.448
610348 | Project A | Area3 | Sub Area 31 | Section 311 | C-10213 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.095393 | 2.3848 | IWP-6013 | 0.8 | 0 | 1.9079 | 78 | 0 | 148.8138 | 1.9079 | 148.8138
610348 | Project A | Area3 | Sub Area 31 | Section 311 | C-10213 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6027 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610348 | Project A | Area3 | Sub Area 31 | Section 311 | C-10213 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610349 | Project A | Area3 | Sub Area 31 | Section 311 | C-10214 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610349 | Project A | Area3 | Sub Area 31 | Section 311 | C-10214 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12316 | 3.079 | IWP-6013 | 0.8 | 0 | 2.4632 | 78 | 0 | 192.1304 | 2.4632 | 192.1304
610349 | Project A | Area3 | Sub Area 31 | Section 311 | C-10214 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6027 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610350 | Project A | Area3 | Sub Area 31 | Section 311 | C-10215 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable6awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.10166 | 2.5416 | IWP-6019 | 0.75 | 1.9062 | 0 | 110 | 209.6808 | 0 | 1.9062 | 209.6808
610350 | Project A | Area3 | Sub Area 31 | Section 311 | C-10215 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6027 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610350 | Project A | Area3 | Sub Area 31 | Section 311 | C-10215 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 2 | 1 |  | 0.26 | 0.52 | IWP-6027 | 0.75 | 0.39 | 0 | 110 | 42.9 | 0 | 0.39 | 42.9
610351 | Project A | Area3 | Sub Area 31 | Section 311 | C-10216 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable1pr16awg Shld 600V ACIC, Random Fill | M | 25 | 1 | Tray | 0.095393 | 2.3848 | IWP-6019 | 0.75 | 1.7886 | 0 | 110 | 196.7489 | 0 | 1.7886 | 196.7489
610351 | Project A | Area3 | Sub Area 31 | Section 311 | C-10216 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6027 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610351 | Project A | Area3 | Sub Area 31 | Section 311 | C-10216 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610352 | Project A | Area3 | Sub Area 31 | Section 311 | C-10217 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610352 | Project A | Area3 | Sub Area 31 | Section 311 | C-10217 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12316 | 3.079 | IWP-6019 | 0.75 | 2.3093 | 0 | 110 | 254.0185 | 0 | 2.3093 | 254.0185
610352 | Project A | Area3 | Sub Area 31 | Section 311 | C-10217 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6027 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610353 | Project A | Area3 | Sub Area 32 | Section 312 | C-10218 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 43 | 1 | Tray | 0.10614 | 4.5641 | IWP-6013 | 0.8 | 0 | 3.6513 | 78 | 0 | 284.8002 | 3.6513 | 284.8002
610353 | Project A | Area3 | Sub Area 32 | Section 312 | C-10218 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610353 | Project A | Area3 | Sub Area 32 | Section 312 | C-10218 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6027 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610354 | Project A | Area3 | Sub Area 32 | Section 312 | C-10219 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 11 | 1 | Tray | 0.14331 | 1.5765 | IWP-6013 | 0.8 | 0 | 1.2612 | 78 | 0 | 98.3708 | 1.2612 | 98.3708
610354 | Project A | Area3 | Sub Area 32 | Section 312 | C-10219 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 1.2 | 2.4 | IWP-6027 | 0.8 | 0 | 1.92 | 78 | 0 | 149.76 | 1.92 | 149.76
610354 | Project A | Area3 | Sub Area 32 | Section 312 | C-10219 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6027 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610355 | Project A | Area3 | Sub Area 32 | Section 312 | C-10220 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 11 | 1 | Tray | 0.14331 | 1.5765 | IWP-6013 | 0.8 | 0 | 1.2612 | 78 | 0 | 98.3708 | 1.2612 | 98.3708
610355 | Project A | Area3 | Sub Area 32 | Section 312 | C-10220 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 1.2 | 2.4 | IWP-6027 | 0.8 | 0 | 1.92 | 78 | 0 | 149.76 | 1.92 | 149.76
610355 | Project A | Area3 | Sub Area 32 | Section 312 | C-10220 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6027 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610356 | Project A | Area3 | Sub Area 32 | Section 312 | P-10205 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 80 | 1 | Tray | 0.095393 | 7.6315 | IWP-6013 | 0.8 | 0 | 6.1052 | 78 | 0 | 476.204 | 6.1052 | 476.204
610356 | Project A | Area3 | Sub Area 32 | Section 312 | P-10205 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610356 | Project A | Area3 | Sub Area 32 | Section 312 | P-10205 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610357 | Project A | Area3 | Sub Area 32 | Section 312 | P-10206 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 80 | 1 | Tray | 0.095393 | 7.6315 | IWP-6013 | 0.8 | 0 | 6.1052 | 78 | 0 | 476.204 | 6.1052 | 476.204
610357 | Project A | Area3 | Sub Area 32 | Section 312 | P-10206 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610357 | Project A | Area3 | Sub Area 32 | Section 312 | P-10206 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610358 | Project A | Area3 | Sub Area 32 | Section 312 | C-10221 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 31 | 1 | Tray | 0.095393 | 2.9572 | IWP-6013 | 0.8 | 0 | 2.3658 | 78 | 0 | 184.5291 | 2.3658 | 184.5291
610358 | Project A | Area3 | Sub Area 32 | Section 312 | C-10221 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610358 | Project A | Area3 | Sub Area 32 | Section 312 | C-10221 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610359 | Project A | Area3 | Sub Area 32 | Section 312 | C-10222 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 31 | 1 | Tray | 0.095393 | 2.9572 | IWP-6013 | 0.8 | 0 | 2.3658 | 78 | 0 | 184.5291 | 2.3658 | 184.5291
610359 | Project A | Area3 | Sub Area 32 | Section 312 | C-10222 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610359 | Project A | Area3 | Sub Area 32 | Section 312 | C-10222 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610360 | Project A | Area3 | Sub Area 32 | Section 312 | C-10223 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 49 | 1 | Tray | 0.095393 | 4.6743 | IWP-6013 | 0.8 | 0 | 3.7394 | 78 | 0 | 291.675 | 3.7394 | 291.675
610360 | Project A | Area3 | Sub Area 32 | Section 312 | C-10223 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610360 | Project A | Area3 | Sub Area 32 | Section 312 | C-10223 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610361 | Project A | Area3 | Sub Area 32 | Section 312 | C-10224 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 49 | 1 | Tray | 0.095393 | 4.6743 | IWP-6013 | 0.8 | 0 | 3.7394 | 78 | 0 | 291.675 | 3.7394 | 291.675
610361 | Project A | Area3 | Sub Area 32 | Section 312 | C-10224 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610361 | Project A | Area3 | Sub Area 32 | Section 312 | C-10224 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610362 | Project A | Area3 | Sub Area 32 | Section 312 | C-10225 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 14 | 1 | Tray | 0.095393 | 1.3355 | IWP-6013 | 0.8 | 0 | 1.0684 | 78 | 0 | 83.3357 | 1.0684 | 83.3357
610362 | Project A | Area3 | Sub Area 32 | Section 312 | C-10225 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610362 | Project A | Area3 | Sub Area 32 | Section 312 | C-10225 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610363 | Project A | Area3 | Sub Area 32 | Section 312 | C-10226 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 23 | 1 | Tray | 0.095393 | 2.194 | IWP-6013 | 0.8 | 0 | 1.7552 | 78 | 0 | 136.9087 | 1.7552 | 136.9087
610363 | Project A | Area3 | Sub Area 32 | Section 312 | C-10226 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610363 | Project A | Area3 | Sub Area 32 | Section 312 | C-10226 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610364 | Project A | Area3 | Sub Area 32 | Section 312 | C-10227 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 15 | 1 | Tray | 0.095393 | 1.4309 | IWP-6014 | 0.8 | 0 | 1.1447 | 78 | 0 | 89.2883 | 1.1447 | 89.2883
610364 | Project A | Area3 | Sub Area 32 | Section 312 | C-10227 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610364 | Project A | Area3 | Sub Area 32 | Section 312 | C-10227 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610365 | Project A | Area3 | Sub Area 32 | Section 312 | C-10228 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 95 | 1 | Tray | 0.095393 | 9.0624 | IWP-6014 | 0.8 | 0 | 7.2499 | 78 | 0 | 565.4923 | 7.2499 | 565.4923
610365 | Project A | Area3 | Sub Area 32 | Section 312 | C-10228 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610365 | Project A | Area3 | Sub Area 32 | Section 312 | C-10228 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610366 | Project A | Area3 | Sub Area 32 | Section 312 | C-10229 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 82 | 1 | Tray | 0.095393 | 7.8223 | IWP-6014 | 0.8 | 0 | 6.2578 | 78 | 0 | 488.1091 | 6.2578 | 488.1091
610366 | Project A | Area3 | Sub Area 32 | Section 312 | C-10229 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610366 | Project A | Area3 | Sub Area 32 | Section 312 | C-10229 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610367 | Project A | Area3 | Sub Area 32 | Section 312 | C-10230 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 92 | 1 | Tray | 0.095393 | 8.7762 | IWP-6014 | 0.8 | 0 | 7.021 | 78 | 0 | 547.6346 | 7.021 | 547.6346
610367 | Project A | Area3 | Sub Area 32 | Section 312 | C-10230 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610367 | Project A | Area3 | Sub Area 32 | Section 312 | C-10230 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610368 | Project A | Area3 | Sub Area 32 | Section 312 | C-10231 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 126 | 1 | Tray | 0.095393 | 12.0196 | IWP-6014 | 0.8 | 0 | 9.6157 | 78 | 0 | 750.0213 | 9.6157 | 750.0213
610368 | Project A | Area3 | Sub Area 32 | Section 312 | C-10231 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610368 | Project A | Area3 | Sub Area 32 | Section 312 | C-10231 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610369 | Project A | Area3 | Sub Area 32 | Section 312 | C-10232 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 100 | 1 | Tray | 0.095393 | 9.5393 | IWP-6014 | 0.8 | 0 | 7.6315 | 78 | 0 | 595.255 | 7.6315 | 595.255
610369 | Project A | Area3 | Sub Area 32 | Section 312 | C-10232 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610369 | Project A | Area3 | Sub Area 32 | Section 312 | C-10232 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610370 | Project A | Area3 | Sub Area 32 | Section 312 | C-10233 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 126 | 1 | Tray | 0.095393 | 12.0196 | IWP-6014 | 0.8 | 0 | 9.6157 | 78 | 0 | 750.0213 | 9.6157 | 750.0213
610370 | Project A | Area3 | Sub Area 32 | Section 312 | C-10233 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610370 | Project A | Area3 | Sub Area 32 | Section 312 | C-10233 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610371 | Project A | Area3 | Sub Area 32 | Section 312 | C-10234 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 143 | 1 | Tray | 0.095393 | 13.6413 | IWP-6014 | 0.8 | 0 | 10.913 | 78 | 0 | 851.2147 | 10.913 | 851.2147
610371 | Project A | Area3 | Sub Area 32 | Section 312 | C-10234 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610371 | Project A | Area3 | Sub Area 32 | Section 312 | C-10234 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610372 | Project A | Area3 | Sub Area 32 | Section 312 | C-10235 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 143 | 1 | Tray | 0.095393 | 13.6413 | IWP-6014 | 0.8 | 0 | 10.913 | 78 | 0 | 851.2147 | 10.913 | 851.2147
610372 | Project A | Area3 | Sub Area 32 | Section 312 | C-10235 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610372 | Project A | Area3 | Sub Area 32 | Section 312 | C-10235 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610373 | Project A | Area3 | Sub Area 32 | Section 312 | C-10236 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 132 | 1 | Tray | 0.095393 | 12.5919 | IWP-6014 | 0.8 | 0 | 10.0735 | 78 | 0 | 785.7366 | 10.0735 | 785.7366
610373 | Project A | Area3 | Sub Area 32 | Section 312 | C-10236 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610373 | Project A | Area3 | Sub Area 32 | Section 312 | C-10236 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610374 | Project A | Area3 | Sub Area 32 | Section 312 | C-10237 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 143 | 1 | Tray | 0.095393 | 13.6413 | IWP-6014 | 0.8 | 0 | 10.913 | 78 | 0 | 851.2147 | 10.913 | 851.2147
610374 | Project A | Area3 | Sub Area 32 | Section 312 | C-10237 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610374 | Project A | Area3 | Sub Area 32 | Section 312 | C-10237 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610375 | Project A | Area3 | Sub Area 32 | Section 312 | C-10238 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 143 | 1 | Tray | 0.095393 | 13.6413 | IWP-6014 | 0.8 | 0 | 10.913 | 78 | 0 | 851.2147 | 10.913 | 851.2147
610375 | Project A | Area3 | Sub Area 32 | Section 312 | C-10238 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610375 | Project A | Area3 | Sub Area 32 | Section 312 | C-10238 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610376 | Project A | Area3 | Sub Area 32 | Section 312 | C-10239 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 143 | 1 | Tray | 0.095393 | 13.6413 | IWP-6014 | 0.8 | 0 | 10.913 | 78 | 0 | 851.2147 | 10.913 | 851.2147
610376 | Project A | Area3 | Sub Area 32 | Section 312 | C-10239 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610376 | Project A | Area3 | Sub Area 32 | Section 312 | C-10239 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610377 | Project A | Area3 | Sub Area 32 | Section 312 | C-10240 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 18 | 1 | Tray | 0.095393 | 1.7171 | IWP-6014 | 0.8 | 0 | 1.3737 | 78 | 0 | 107.1459 | 1.3737 | 107.1459
610377 | Project A | Area3 | Sub Area 32 | Section 312 | C-10240 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610377 | Project A | Area3 | Sub Area 32 | Section 312 | C-10240 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610378 | Project A | Area3 | Sub Area 32 | Section 312 | C-10241 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 18 | 1 | Tray | 0.095393 | 1.7171 | IWP-6014 | 0.8 | 0 | 1.3737 | 78 | 0 | 107.1459 | 1.3737 | 107.1459
610378 | Project A | Area3 | Sub Area 32 | Section 312 | C-10241 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610378 | Project A | Area3 | Sub Area 32 | Section 312 | C-10241 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610379 | Project A | Area3 | Sub Area 32 | Section 312 | C-10242 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 18 | 1 | Tray | 0.095393 | 1.7171 | IWP-6014 | 0.8 | 0 | 1.3737 | 78 | 0 | 107.1459 | 1.3737 | 107.1459
610379 | Project A | Area3 | Sub Area 32 | Section 312 | C-10242 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610379 | Project A | Area3 | Sub Area 32 | Section 312 | C-10242 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610380 | Project A | Area3 | Sub Area 32 | Section 312 | C-10243 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 20 | 1 | Tray | 0.095393 | 1.9079 | IWP-6014 | 0.8 | 0 | 1.5263 | 78 | 0 | 119.051 | 1.5263 | 119.051
610380 | Project A | Area3 | Sub Area 32 | Section 312 | C-10243 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610380 | Project A | Area3 | Sub Area 32 | Section 312 | C-10243 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610381 | Project A | Area3 | Sub Area 32 | Section 312 | C-10244 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.095393 | 2.3848 | IWP-6014 | 0.8 | 0 | 1.9079 | 78 | 0 | 148.8138 | 1.9079 | 148.8138
610381 | Project A | Area3 | Sub Area 32 | Section 312 | C-10244 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610381 | Project A | Area3 | Sub Area 32 | Section 312 | C-10244 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610382 | Project A | Area3 | Sub Area 32 | Section 312 | C-10245 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 23 | 1 | Tray | 0.095393 | 2.194 | IWP-6014 | 0.8 | 0 | 1.7552 | 78 | 0 | 136.9087 | 1.7552 | 136.9087
610382 | Project A | Area3 | Sub Area 32 | Section 312 | C-10245 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610382 | Project A | Area3 | Sub Area 32 | Section 312 | C-10245 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610383 | Project A | Area3 | Sub Area 32 | Section 312 | C-10246 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 23 | 1 | Tray | 0.095393 | 2.194 | IWP-6014 | 0.8 | 0 | 1.7552 | 78 | 0 | 136.9087 | 1.7552 | 136.9087
610383 | Project A | Area3 | Sub Area 32 | Section 312 | C-10246 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610383 | Project A | Area3 | Sub Area 32 | Section 312 | C-10246 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610384 | Project A | Area3 | Sub Area 32 | Section 312 | C-10247 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 23 | 1 | Tray | 0.095393 | 2.194 | IWP-6014 | 0.8 | 0 | 1.7552 | 78 | 0 | 136.9087 | 1.7552 | 136.9087
610384 | Project A | Area3 | Sub Area 32 | Section 312 | C-10247 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610384 | Project A | Area3 | Sub Area 32 | Section 312 | C-10247 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610385 | Project A | Area3 | Sub Area 32 | Section 312 | C-10248 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 18 | 1 | Tray | 0.095393 | 1.7171 | IWP-6014 | 0.8 | 0 | 1.3737 | 78 | 0 | 107.1459 | 1.3737 | 107.1459
610385 | Project A | Area3 | Sub Area 32 | Section 312 | C-10248 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610385 | Project A | Area3 | Sub Area 32 | Section 312 | C-10248 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610386 | Project A | Area3 | Sub Area 32 | Section 312 | C-10249 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6014 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610386 | Project A | Area3 | Sub Area 32 | Section 312 | C-10249 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610386 | Project A | Area3 | Sub Area 32 | Section 312 | C-10249 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610387 | Project A | Area3 | Sub Area 32 | Section 312 | C-10250 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6014 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610387 | Project A | Area3 | Sub Area 32 | Section 312 | C-10250 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610387 | Project A | Area3 | Sub Area 32 | Section 312 | C-10250 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610388 | Project A | Area3 | Sub Area 32 | Section 312 | C-10251 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6014 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610388 | Project A | Area3 | Sub Area 32 | Section 312 | C-10251 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610388 | Project A | Area3 | Sub Area 32 | Section 312 | C-10251 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610389 | Project A | Area3 | Sub Area 32 | Section 312 | C-10252 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6014 | 0.8 | 0 | 0.76315 | 78 | 0 | 59.5255 | 0.76315 | 59.5255
610389 | Project A | Area3 | Sub Area 32 | Section 312 | C-10252 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610389 | Project A | Area3 | Sub Area 32 | Section 312 | C-10252 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610390 | Project A | Area3 | Sub Area 32 | Section 312 | C-10253 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 11 | 1 | Tray | 0.095393 | 1.0493 | IWP-6014 | 0.8 | 0 | 0.83946 | 78 | 0 | 65.4781 | 0.83946 | 65.4781
610390 | Project A | Area3 | Sub Area 32 | Section 312 | C-10253 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610390 | Project A | Area3 | Sub Area 32 | Section 312 | C-10253 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610391 | Project A | Area3 | Sub Area 32 | Section 312 | C-10254 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 15 | 1 | Tray | 0.095393 | 1.4309 | IWP-6014 | 0.8 | 0 | 1.1447 | 78 | 0 | 89.2883 | 1.1447 | 89.2883
610391 | Project A | Area3 | Sub Area 32 | Section 312 | C-10254 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610391 | Project A | Area3 | Sub Area 32 | Section 312 | C-10254 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610392 | Project A | Area3 | Sub Area 32 | Section 312 | C-10255 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 11 | 1 | Tray | 0.095393 | 1.0493 | IWP-6014 | 0.8 | 0 | 0.83946 | 78 | 0 | 65.4781 | 0.83946 | 65.4781
610392 | Project A | Area3 | Sub Area 32 | Section 312 | C-10255 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610392 | Project A | Area3 | Sub Area 32 | Section 312 | C-10255 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6027 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610393 | Project A | Area3 | Sub Area 32 | Section 312 | P-10127 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.14878 | 1.4878 | IWP-6014 | 0.8 | 0 | 1.1902 | 78 | 0 | 92.8374 | 1.1902 | 92.8374
610393 | Project A | Area3 | Sub Area 32 | Section 312 | P-10127 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610393 | Project A | Area3 | Sub Area 32 | Section 312 | P-10127 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610394 | Project A | Area3 | Sub Area 32 | Section 312 | C-10256 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.13257 | 0.66283 | IWP-6014 | 0.8 | 0 | 0.53026 | 78 | 0 | 41.3604 | 0.53026 | 41.3604
610394 | Project A | Area3 | Sub Area 32 | Section 312 | C-10256 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610394 | Project A | Area3 | Sub Area 32 | Section 312 | C-10256 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6027 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610395 | Project A | Area3 | Sub Area 32 | Section 312 | C-10257 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.13257 | 0.66283 | IWP-6014 | 0.8 | 0 | 0.53026 | 78 | 0 | 41.3604 | 0.53026 | 41.3604
610395 | Project A | Area3 | Sub Area 32 | Section 312 | C-10257 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610395 | Project A | Area3 | Sub Area 32 | Section 312 | C-10257 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6027 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610396 | Project A | Area3 | Sub Area 32 | Section 312 | C-10258 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.13257 | 0.66283 | IWP-6014 | 0.8 | 0 | 0.53026 | 78 | 0 | 41.3604 | 0.53026 | 41.3604
610396 | Project A | Area3 | Sub Area 32 | Section 312 | C-10258 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610396 | Project A | Area3 | Sub Area 32 | Section 312 | C-10258 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6027 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610397 | Project A | Area3 | Sub Area 32 | Section 312 | C-10259 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.13257 | 0.66283 | IWP-6014 | 0.8 | 0 | 0.53026 | 78 | 0 | 41.3604 | 0.53026 | 41.3604
610397 | Project A | Area3 | Sub Area 32 | Section 312 | C-10259 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610397 | Project A | Area3 | Sub Area 32 | Section 312 | C-10259 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6027 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610398 | Project A | Area3 | Sub Area 32 | Section 312 | C-10260 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.13257 | 0.66283 | IWP-6014 | 0.8 | 0 | 0.53026 | 78 | 0 | 41.3604 | 0.53026 | 41.3604
610398 | Project A | Area3 | Sub Area 32 | Section 312 | C-10260 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610398 | Project A | Area3 | Sub Area 32 | Section 312 | C-10260 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6027 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610399 | Project A | Area3 | Sub Area 32 | Section 312 | C-10261 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.13257 | 0.66283 | IWP-6014 | 0.8 | 0 | 0.53026 | 78 | 0 | 41.3604 | 0.53026 | 41.3604
610399 | Project A | Area3 | Sub Area 32 | Section 312 | C-10261 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610399 | Project A | Area3 | Sub Area 32 | Section 312 | C-10261 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6027 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610400 | Project A | Area3 | Sub Area 32 | Section 312 | P-10128 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.14878 | 1.4878 | IWP-6014 | 0.8 | 0 | 1.1902 | 78 | 0 | 92.8374 | 1.1902 | 92.8374
610400 | Project A | Area3 | Sub Area 32 | Section 312 | P-10128 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610400 | Project A | Area3 | Sub Area 32 | Section 312 | P-10128 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610401 | Project A | Area3 | Sub Area 32 | Section 312 | P-10129 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.14878 | 1.4878 | IWP-6014 | 0.8 | 0 | 1.1902 | 78 | 0 | 92.8374 | 1.1902 | 92.8374
610401 | Project A | Area3 | Sub Area 32 | Section 312 | P-10129 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610401 | Project A | Area3 | Sub Area 32 | Section 312 | P-10129 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610402 | Project A | Area3 | Sub Area 32 | Section 312 | P-10130 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.14878 | 0.74389 | IWP-6014 | 0.8 | 0 | 0.59511 | 78 | 0 | 46.4187 | 0.59511 | 46.4187
610402 | Project A | Area3 | Sub Area 32 | Section 312 | P-10130 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610402 | Project A | Area3 | Sub Area 32 | Section 312 | P-10130 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610403 | Project A | Area3 | Sub Area 32 | Section 312 | P-10131 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.14878 | 2.2317 | IWP-6014 | 0.8 | 0 | 1.7853 | 78 | 0 | 139.2561 | 1.7853 | 139.2561
610403 | Project A | Area3 | Sub Area 32 | Section 312 | P-10131 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610403 | Project A | Area3 | Sub Area 32 | Section 312 | P-10131 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610404 | Project A | Area3 | Sub Area 32 | Section 312 | P-10132 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 45 | 1 | Tray | 0.14878 | 6.695 | IWP-6014 | 0.8 | 0 | 5.356 | 78 | 0 | 417.7683 | 5.356 | 417.7683
610404 | Project A | Area3 | Sub Area 32 | Section 312 | P-10132 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610404 | Project A | Area3 | Sub Area 32 | Section 312 | P-10132 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610405 | Project A | Area3 | Sub Area 32 | Section 312 | P-10133 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 50 | 1 | Tray | 0.14878 | 7.4389 | IWP-6014 | 0.8 | 0 | 5.9511 | 78 | 0 | 464.187 | 5.9511 | 464.187
610405 | Project A | Area3 | Sub Area 32 | Section 312 | P-10133 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610405 | Project A | Area3 | Sub Area 32 | Section 312 | P-10133 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610406 | Project A | Area3 | Sub Area 32 | Section 312 | P-10134 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 70 | 1 | Tray | 0.14878 | 10.4145 | IWP-6014 | 0.8 | 0 | 8.3316 | 78 | 0 | 649.8619 | 8.3316 | 649.8619
610406 | Project A | Area3 | Sub Area 32 | Section 312 | P-10134 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610406 | Project A | Area3 | Sub Area 32 | Section 312 | P-10134 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610407 | Project A | Area3 | Sub Area 32 | Section 312 | P-10136 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg | M | 15 | 1 | Tray | 0.14878 | 2.2317 | IWP-6014 | 0.8 | 0 | 1.7853 | 78 | 0 | 139.2561 | 1.7853 | 139.2561
610407 | Project A | Area3 | Sub Area 32 | Section 312 | P-10136 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610407 | Project A | Area3 | Sub Area 32 | Section 312 | P-10136 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610408 | Project A | Area3 | Sub Area 32 | Section 312 | P-10137 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.14878 | 0.74389 | IWP-6014 | 0.8 | 0 | 0.59511 | 78 | 0 | 46.4187 | 0.59511 | 46.4187
610408 | Project A | Area3 | Sub Area 32 | Section 312 | P-10137 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610408 | Project A | Area3 | Sub Area 32 | Section 312 | P-10137 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610409 | Project A | Area3 | Sub Area 32 | Section 312 | P-10138 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 14 | 1 | Tray | 0.14878 | 2.0829 | IWP-6014 | 0.8 | 0 | 1.6663 | 78 | 0 | 129.9724 | 1.6663 | 129.9724
610409 | Project A | Area3 | Sub Area 32 | Section 312 | P-10138 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610409 | Project A | Area3 | Sub Area 32 | Section 312 | P-10138 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610410 | Project A | Area3 | Sub Area 32 | Section 312 | P-10139 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.14878 | 2.2317 | IWP-6014 | 0.8 | 0 | 1.7853 | 78 | 0 | 139.2561 | 1.7853 | 139.2561
610410 | Project A | Area3 | Sub Area 32 | Section 312 | P-10139 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610410 | Project A | Area3 | Sub Area 32 | Section 312 | P-10139 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610411 | Project A | Area3 | Sub Area 32 | Section 312 | P-10140 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.14878 | 2.2317 | IWP-6014 | 0.8 | 0 | 1.7853 | 78 | 0 | 139.2561 | 1.7853 | 139.2561
610411 | Project A | Area3 | Sub Area 32 | Section 312 | P-10140 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610411 | Project A | Area3 | Sub Area 32 | Section 312 | P-10140 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610412 | Project A | Area3 | Sub Area 32 | Section 312 | P-10141 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 13 | 1 | Tray | 0.14878 | 1.9341 | IWP-6014 | 0.8 | 0 | 1.5473 | 78 | 0 | 120.6886 | 1.5473 | 120.6886
610412 | Project A | Area3 | Sub Area 32 | Section 312 | P-10141 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610412 | Project A | Area3 | Sub Area 32 | Section 312 | P-10141 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610413 | Project A | Area3 | Sub Area 32 | Section 312 | P-10142 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 16 | 1 | Tray | 0.14878 | 2.3804 | IWP-6014 | 0.8 | 0 | 1.9044 | 78 | 0 | 148.5399 | 1.9044 | 148.5399
610413 | Project A | Area3 | Sub Area 32 | Section 312 | P-10142 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610413 | Project A | Area3 | Sub Area 32 | Section 312 | P-10142 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610414 | Project A | Area3 | Sub Area 32 | Section 312 | P-10143 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 31 | 1 | Tray | 0.14878 | 4.6121 | IWP-6014 | 0.8 | 0 | 3.6897 | 78 | 0 | 287.796 | 3.6897 | 287.796
610414 | Project A | Area3 | Sub Area 32 | Section 312 | P-10143 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.816 | 1.632 | IWP-6027 | 0.8 | 0 | 1.3056 | 78 | 0 | 101.8368 | 1.3056 | 101.8368
610414 | Project A | Area3 | Sub Area 32 | Section 312 | P-10143 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.176 | 0.704 | IWP-6027 | 0.8 | 0 | 0.5632 | 78 | 0 | 43.9296 | 0.5632 | 43.9296
610415 | Project A | Area4 | Sub Area 41 | Section 411 | C-10262 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable6pr16awg Shld 300V ACIC, Random Fill | M | 76 | 1 | Tray | 0.16974 | 12.9001 | IWP-6014 | 0.8 | 0 | 10.32 | 78 | 0 | 804.9636 | 10.32 | 804.9636
610415 | Project A | Area4 | Sub Area 41 | Section 411 | C-10262 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6027 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610415 | Project A | Area4 | Sub Area 41 | Section 411 | C-10262 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6027 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610416 | Project A | Area4 | Sub Area 41 | Section 411 | C-10263 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 76 | 1 | Tray | 0.22572 | 17.1547 | IWP-6015 | 0.8 | 0 | 13.7238 | 78 | 0 | 1070.4531 | 13.7238 | 1070.4531
610416 | Project A | Area4 | Sub Area 41 | Section 411 | C-10263 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6027 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610416 | Project A | Area4 | Sub Area 41 | Section 411 | C-10263 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6027 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610417 | Project A | Area4 | Sub Area 41 | Section 411 | C-10264 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 76 | 1 | Tray | 0.22572 | 17.1547 | IWP-6015 | 0.8 | 0 | 13.7238 | 78 | 0 | 1070.4531 | 13.7238 | 1070.4531
610417 | Project A | Area4 | Sub Area 41 | Section 411 | C-10264 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6027 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610417 | Project A | Area4 | Sub Area 41 | Section 411 | C-10264 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6027 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610418 | Project A | Area4 | Sub Area 41 | Section 411 | C-10265 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 76 | 1 | Tray | 0.22572 | 17.1547 | IWP-6015 | 0.8 | 0 | 13.7238 | 78 | 0 | 1070.4531 | 13.7238 | 1070.4531
610418 | Project A | Area4 | Sub Area 41 | Section 411 | C-10265 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6027 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610418 | Project A | Area4 | Sub Area 41 | Section 411 | C-10265 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6027 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610419 | Project A | Area4 | Sub Area 41 | Section 411 | C-10266 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 76 | 1 | Tray | 0.22572 | 17.1547 | IWP-6015 | 0.8 | 0 | 13.7238 | 78 | 0 | 1070.4531 | 13.7238 | 1070.4531
610419 | Project A | Area4 | Sub Area 41 | Section 411 | C-10266 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6027 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610419 | Project A | Area4 | Sub Area 41 | Section 411 | C-10266 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6027 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610420 | Project A | Area4 | Sub Area 41 | Section 411 | C-10267 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 76 | 1 | Tray | 0.22572 | 17.1547 | IWP-6015 | 0.8 | 0 | 13.7238 | 78 | 0 | 1070.4531 | 13.7238 | 1070.4531
610420 | Project A | Area4 | Sub Area 41 | Section 411 | C-10267 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6027 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610420 | Project A | Area4 | Sub Area 41 | Section 411 | C-10267 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6027 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610421 | Project A | Area4 | Sub Area 41 | Section 411 | C-10268 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 76 | 1 | Tray | 0.22572 | 17.1547 | IWP-6015 | 0.8 | 0 | 13.7238 | 78 | 0 | 1070.4531 | 13.7238 | 1070.4531
610421 | Project A | Area4 | Sub Area 41 | Section 411 | C-10268 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6027 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610421 | Project A | Area4 | Sub Area 41 | Section 411 | C-10268 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6027 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610422 | Project A | Area4 | Sub Area 41 | Section 411 | C-10269 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 76 | 1 | Tray | 0.22572 | 17.1547 | IWP-6015 | 0.8 | 0 | 13.7238 | 78 | 0 | 1070.4531 | 13.7238 | 1070.4531
610422 | Project A | Area4 | Sub Area 41 | Section 411 | C-10269 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610422 | Project A | Area4 | Sub Area 41 | Section 411 | C-10269 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610423 | Project A | Area4 | Sub Area 41 | Section 411 | C-10270 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 290 | 1 | Tray | 0.19079 | 55.3282 | IWP-6015 | 0.8 | 0 | 44.2626 | 78 | 0 | 3452.4797 | 44.2626 | 3452.4797
610423 | Project A | Area4 | Sub Area 41 | Section 411 | C-10270 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610423 | Project A | Area4 | Sub Area 41 | Section 411 | C-10270 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6028 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610424 | Project A | Area4 | Sub Area 41 | Section 411 | C-10271 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 290 | 1 | Tray | 0.14331 | 41.5611 | IWP-6015 | 0.8 | 0 | 33.2489 | 78 | 0 | 2593.412 | 33.2489 | 2593.412
610424 | Project A | Area4 | Sub Area 41 | Section 411 | C-10271 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610424 | Project A | Area4 | Sub Area 41 | Section 411 | C-10271 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6028 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610425 | Project A | Area4 | Sub Area 41 | Section 411 | C-10272 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4triad 16awg Shld 300V ACIC, Random Fill | M | 290 | 1 | Tray | 0.16974 | 49.2239 | IWP-6015 | 0.8 | 0 | 39.3791 | 78 | 0 | 3071.5716 | 39.3791 | 3071.5716
610425 | Project A | Area4 | Sub Area 41 | Section 411 | C-10272 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610425 | Project A | Area4 | Sub Area 41 | Section 411 | C-10272 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6028 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610426 | Project A | Area4 | Sub Area 41 | Section 411 | C-10273 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 290 | 1 | Tray | 0.22572 | 65.4587 | IWP-6015 | 0.8 | 0 | 52.367 | 78 | 0 | 4084.6237 | 52.367 | 4084.6237
610426 | Project A | Area4 | Sub Area 41 | Section 411 | C-10273 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610426 | Project A | Area4 | Sub Area 41 | Section 411 | C-10273 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610427 | Project A | Area4 | Sub Area 41 | Section 411 | C-10274 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 156 | 1 | Tray | 0.22572 | 35.2123 | IWP-6015 | 0.8 | 0 | 28.1698 | 78 | 0 | 2197.2458 | 28.1698 | 2197.2458
610427 | Project A | Area4 | Sub Area 41 | Section 411 | C-10274 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610427 | Project A | Area4 | Sub Area 41 | Section 411 | C-10274 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610428 | Project A | Area4 | Sub Area 41 | Section 411 | C-10275 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 152 | 1 | Tray | 0.19079 | 28.9996 | IWP-6015 | 0.8 | 0 | 23.1997 | 78 | 0 | 1809.5756 | 23.1997 | 1809.5756
610428 | Project A | Area4 | Sub Area 41 | Section 411 | C-10275 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610428 | Project A | Area4 | Sub Area 41 | Section 411 | C-10275 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6028 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610429 | Project A | Area4 | Sub Area 41 | Section 411 | C-10276 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 152 | 1 | Tray | 0.22572 | 34.3094 | IWP-6015 | 0.8 | 0 | 27.4475 | 78 | 0 | 2140.9062 | 27.4475 | 2140.9062
610429 | Project A | Area4 | Sub Area 41 | Section 411 | C-10276 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610429 | Project A | Area4 | Sub Area 41 | Section 411 | C-10276 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610430 | Project A | Area4 | Sub Area 41 | Section 411 | C-10277 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 152 | 1 | Tray | 0.22572 | 34.3094 | IWP-6015 | 0.8 | 0 | 27.4475 | 78 | 0 | 2140.9062 | 27.4475 | 2140.9062
610430 | Project A | Area4 | Sub Area 41 | Section 411 | C-10277 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610430 | Project A | Area4 | Sub Area 41 | Section 411 | C-10277 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610431 | Project A | Area4 | Sub Area 41 | Section 411 | C-10278 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 152 | 1 | Tray | 0.22572 | 34.3094 | IWP-6015 | 0.8 | 0 | 27.4475 | 78 | 0 | 2140.9062 | 27.4475 | 2140.9062
610431 | Project A | Area4 | Sub Area 41 | Section 411 | C-10278 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610431 | Project A | Area4 | Sub Area 41 | Section 411 | C-10278 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610432 | Project A | Area4 | Sub Area 41 | Section 411 | C-10279 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 152 | 1 | Tray | 0.22572 | 34.3094 | IWP-6016 | 0.8 | 0 | 27.4475 | 78 | 0 | 2140.9062 | 27.4475 | 2140.9062
610432 | Project A | Area4 | Sub Area 41 | Section 411 | C-10279 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610432 | Project A | Area4 | Sub Area 41 | Section 411 | C-10279 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610433 | Project A | Area4 | Sub Area 41 | Section 411 | C-10280 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable6pr16awg Shld 300V ACIC, Random Fill | M | 178 | 1 | Tray | 0.16974 | 30.2133 | IWP-6016 | 0.8 | 0 | 24.1706 | 78 | 0 | 1885.3095 | 24.1706 | 1885.3095
610433 | Project A | Area4 | Sub Area 41 | Section 411 | C-10280 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610433 | Project A | Area4 | Sub Area 41 | Section 411 | C-10280 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6028 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610434 | Project A | Area4 | Sub Area 41 | Section 411 | C-10281 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 184 | 1 | Tray | 0.23692 | 43.5926 | IWP-6016 | 0.8 | 0 | 34.874 | 78 | 0 | 2720.1759 | 34.874 | 2720.1759
610434 | Project A | Area4 | Sub Area 41 | Section 411 | C-10281 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6028 | 0.8 | 0 | 3.3072 | 78 | 0 | 257.9616 | 3.3072 | 257.9616
610434 | Project A | Area4 | Sub Area 41 | Section 411 | C-10281 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6028 | 0.8 | 0 | 6.336 | 78 | 0 | 494.208 | 6.336 | 494.208
610435 | Project A | Area4 | Sub Area 41 | Section 411 | C-10282 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg | M | 5 | 1 | Tray | 0.12988 | 0.64939 | IWP-6019 | 0.75 | 0.48704 | 0 | 110 | 53.5748 | 0 | 0.48704 | 53.5748
610435 | Project A | Area4 | Sub Area 41 | Section 411 | C-10282 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6028 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610435 | Project A | Area4 | Sub Area 41 | Section 411 | C-10282 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6028 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610436 | Project A | Area4 | Sub Area 41 | Section 411 | C-10283 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg | M | 5 | 1 | Tray | 0.12988 | 0.64939 | IWP-6019 | 0.75 | 0.48704 | 0 | 110 | 53.5748 | 0 | 0.48704 | 53.5748
610436 | Project A | Area4 | Sub Area 41 | Section 411 | C-10283 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6028 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610436 | Project A | Area4 | Sub Area 41 | Section 411 | C-10283 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6028 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610437 | Project A | Area4 | Sub Area 41 | Section 411 | C-10284 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg | M | 10 | 1 | Tray | 0.12988 | 1.2988 | IWP-6019 | 0.75 | 0.97409 | 0 | 110 | 107.1497 | 0 | 0.97409 | 107.1497
610437 | Project A | Area4 | Sub Area 41 | Section 411 | C-10284 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6028 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610437 | Project A | Area4 | Sub Area 41 | Section 411 | C-10284 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6028 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610438 | Project A | Area4 | Sub Area 41 | Section 411 | C-10285 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6028 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610438 | Project A | Area4 | Sub Area 41 | Section 411 | C-10285 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg | M | 18 | 1 | Tray | 0.12316 | 2.2169 | IWP-6019 | 0.75 | 1.6627 | 0 | 110 | 182.8933 | 0 | 1.6627 | 182.8933
610438 | Project A | Area4 | Sub Area 41 | Section 411 | C-10285 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6028 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610439 | Project A | Area4 | Sub Area 41 | Section 411 | C-10286 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6019 | 0.75 | 2.4352 | 0 | 110 | 267.8742 | 0 | 2.4352 | 267.8742
610439 | Project A | Area4 | Sub Area 41 | Section 411 | C-10286 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6028 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610439 | Project A | Area4 | Sub Area 41 | Section 411 | C-10286 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6028 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610440 | Project A | Area4 | Sub Area 41 | Section 411 | C-10287 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 166 | 1 | Tray | 0.14331 | 23.7901 | IWP-6016 | 0.8 | 0 | 19.0321 | 78 | 0 | 1484.5048 | 19.0321 | 1484.5048
610440 | Project A | Area4 | Sub Area 41 | Section 411 | C-10287 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610440 | Project A | Area4 | Sub Area 41 | Section 411 | C-10287 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6028 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610441 | Project A | Area4 | Sub Area 41 | Section 411 | C-10288 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 166 | 1 | Tray | 0.22572 | 37.4695 | IWP-6016 | 0.8 | 0 | 29.9756 | 78 | 0 | 2338.0949 | 29.9756 | 2338.0949
610441 | Project A | Area4 | Sub Area 41 | Section 411 | C-10288 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610441 | Project A | Area4 | Sub Area 41 | Section 411 | C-10288 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610442 | Project A | Area4 | Sub Area 41 | Section 411 | C-10289 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 166 | 1 | Tray | 0.22572 | 37.4695 | IWP-6016 | 0.8 | 0 | 29.9756 | 78 | 0 | 2338.0949 | 29.9756 | 2338.0949
610442 | Project A | Area4 | Sub Area 41 | Section 411 | C-10289 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610442 | Project A | Area4 | Sub Area 41 | Section 411 | C-10289 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610443 | Project A | Area4 | Sub Area 41 | Section 411 | C-10290 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 166 | 1 | Tray | 0.22572 | 37.4695 | IWP-6016 | 0.8 | 0 | 29.9756 | 78 | 0 | 2338.0949 | 29.9756 | 2338.0949
610443 | Project A | Area4 | Sub Area 41 | Section 411 | C-10290 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610443 | Project A | Area4 | Sub Area 41 | Section 411 | C-10290 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610444 | Project A | Area4 | Sub Area 41 | Section 411 | C-10291 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 85 | 1 | Tray | 0.22572 | 19.1862 | IWP-6016 | 0.8 | 0 | 15.3489 | 78 | 0 | 1197.2173 | 15.3489 | 1197.2173
610444 | Project A | Area4 | Sub Area 41 | Section 411 | C-10291 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610444 | Project A | Area4 | Sub Area 41 | Section 411 | C-10291 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610445 | Project A | Area4 | Sub Area 41 | Section 411 | C-10292 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 85 | 1 | Tray | 0.22572 | 19.1862 | IWP-6016 | 0.8 | 0 | 15.3489 | 78 | 0 | 1197.2173 | 15.3489 | 1197.2173
610445 | Project A | Area4 | Sub Area 41 | Section 411 | C-10292 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610445 | Project A | Area4 | Sub Area 41 | Section 411 | C-10292 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610446 | Project A | Area4 | Sub Area 41 | Section 411 | C-10293 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 85 | 1 | Tray | 0.22572 | 19.1862 | IWP-6016 | 0.8 | 0 | 15.3489 | 78 | 0 | 1197.2173 | 15.3489 | 1197.2173
610446 | Project A | Area4 | Sub Area 41 | Section 411 | C-10293 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610446 | Project A | Area4 | Sub Area 41 | Section 411 | C-10293 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610447 | Project A | Area4 | Sub Area 41 | Section 411 | C-10294 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 85 | 1 | Tray | 0.22572 | 19.1862 | IWP-6016 | 0.8 | 0 | 15.3489 | 78 | 0 | 1197.2173 | 15.3489 | 1197.2173
610447 | Project A | Area4 | Sub Area 41 | Section 411 | C-10294 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610447 | Project A | Area4 | Sub Area 41 | Section 411 | C-10294 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610448 | Project A | Area4 | Sub Area 41 | Section 411 | C-10295 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 85 | 1 | Tray | 0.22572 | 19.1862 | IWP-6016 | 0.8 | 0 | 15.3489 | 78 | 0 | 1197.2173 | 15.3489 | 1197.2173
610448 | Project A | Area4 | Sub Area 41 | Section 411 | C-10295 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610448 | Project A | Area4 | Sub Area 41 | Section 411 | C-10295 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610449 | Project A | Area4 | Sub Area 41 | Section 411 | C-10296 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 85 | 1 | Tray | 0.22572 | 19.1862 | IWP-6016 | 0.8 | 0 | 15.3489 | 78 | 0 | 1197.2173 | 15.3489 | 1197.2173
610449 | Project A | Area4 | Sub Area 41 | Section 411 | C-10296 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610449 | Project A | Area4 | Sub Area 41 | Section 411 | C-10296 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610450 | Project A | Area4 | Sub Area 41 | Section 411 | C-10297 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 85 | 1 | Tray | 0.22572 | 19.1862 | IWP-6016 | 0.8 | 0 | 15.3489 | 78 | 0 | 1197.2173 | 15.3489 | 1197.2173
610450 | Project A | Area4 | Sub Area 41 | Section 411 | C-10297 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610450 | Project A | Area4 | Sub Area 41 | Section 411 | C-10297 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610451 | Project A | Area4 | Sub Area 41 | Section 411 | C-10298 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 85 | 1 | Tray | 0.19079 | 16.2169 | IWP-6016 | 0.8 | 0 | 12.9735 | 78 | 0 | 1011.9337 | 12.9735 | 1011.9337
610451 | Project A | Area4 | Sub Area 41 | Section 411 | C-10298 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610451 | Project A | Area4 | Sub Area 41 | Section 411 | C-10298 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6028 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610452 | Project A | Area4 | Sub Area 41 | Section 411 | C-10299 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 85 | 1 | Tray | 0.19079 | 16.2169 | IWP-6016 | 0.8 | 0 | 12.9735 | 78 | 0 | 1011.9337 | 12.9735 | 1011.9337
610452 | Project A | Area4 | Sub Area 41 | Section 411 | C-10299 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610452 | Project A | Area4 | Sub Area 41 | Section 411 | C-10299 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6028 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610453 | Project A | Area4 | Sub Area 41 | Section 411 | C-10300 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 85 | 1 | Tray | 0.14331 | 12.1817 | IWP-6016 | 0.8 | 0 | 9.7454 | 78 | 0 | 760.138 | 9.7454 | 760.138
610453 | Project A | Area4 | Sub Area 41 | Section 411 | C-10300 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610453 | Project A | Area4 | Sub Area 41 | Section 411 | C-10300 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6028 | 0.8 | 0 | 1.6896 | 78 | 0 | 131.7888 | 1.6896 | 131.7888
610454 | Project A | Area4 | Sub Area 41 | Section 411 | C-10301 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 85 | 1 | Tray | 0.1946 | 16.5412 | IWP-6016 | 0.8 | 0 | 13.233 | 78 | 0 | 1032.1722 | 13.233 | 1032.1722
610454 | Project A | Area4 | Sub Area 41 | Section 411 | C-10301 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610454 | Project A | Area4 | Sub Area 41 | Section 411 | C-10301 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6028 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610455 | Project A | Area4 | Sub Area 41 | Section 411 | C-10302 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 85 | 1 | Tray | 0.1946 | 16.5412 | IWP-6016 | 0.8 | 0 | 13.233 | 78 | 0 | 1032.1722 | 13.233 | 1032.1722
610455 | Project A | Area4 | Sub Area 41 | Section 411 | C-10302 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610455 | Project A | Area4 | Sub Area 41 | Section 411 | C-10302 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6028 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610456 | Project A | Area4 | Sub Area 41 | Section 411 | C-10303 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable6pr16awg Shld 300V ACIC, Random Fill | M | 100 | 1 | Tray | 0.16974 | 16.9738 | IWP-6016 | 0.8 | 0 | 13.579 | 78 | 0 | 1059.1626 | 13.579 | 1059.1626
610456 | Project A | Area4 | Sub Area 41 | Section 411 | C-10303 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610456 | Project A | Area4 | Sub Area 41 | Section 411 | C-10303 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6028 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610457 | Project A | Area4 | Sub Area 41 | Section 411 | C-10304 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 81 | 1 | Tray | 0.22572 | 18.2833 | IWP-6017 | 0.8 | 0 | 14.6266 | 78 | 0 | 1140.8777 | 14.6266 | 1140.8777
610457 | Project A | Area4 | Sub Area 41 | Section 411 | C-10304 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610457 | Project A | Area4 | Sub Area 41 | Section 411 | C-10304 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610458 | Project A | Area4 | Sub Area 41 | Section 411 | C-10305 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable6pr16awg Shld 300V ACIC, Random Fill | M | 126 | 1 | Tray | 0.16974 | 21.3869 | IWP-6017 | 0.8 | 0 | 17.1096 | 78 | 0 | 1334.5449 | 17.1096 | 1334.5449
610458 | Project A | Area4 | Sub Area 41 | Section 411 | C-10305 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6028 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610458 | Project A | Area4 | Sub Area 41 | Section 411 | C-10305 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6028 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610459 | Project A | Area4 | Sub Area 41 | Section 411 | C-10306 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 97 | 1 | Tray | 0.22572 | 21.8948 | IWP-6017 | 0.8 | 0 | 17.5158 | 78 | 0 | 1366.2362 | 17.5158 | 1366.2362
610459 | Project A | Area4 | Sub Area 41 | Section 411 | C-10306 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6028 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610459 | Project A | Area4 | Sub Area 41 | Section 411 | C-10306 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610460 | Project A | Area4 | Sub Area 41 | Section 411 | C-10307 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable6pr16awg Shld 300V ACIC, Random Fill | M | 138 | 1 | Tray | 0.16974 | 23.4238 | IWP-6028 | 0.8 | 0 | 18.739 | 78 | 0 | 1461.6444 | 18.739 | 1461.6444
610460 | Project A | Area4 | Sub Area 41 | Section 411 | C-10307 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6017 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610460 | Project A | Area4 | Sub Area 41 | Section 411 | C-10307 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 24 | 1 |  | 0.132 | 3.168 | IWP-6028 | 0.8 | 0 | 2.5344 | 78 | 0 | 197.6832 | 2.5344 | 197.6832
610461 | Project A | Area4 | Sub Area 41 | Section 411 | C-10308 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 132 | 1 | Tray | 0.22572 | 29.795 | IWP-6028 | 0.8 | 0 | 23.836 | 78 | 0 | 1859.208 | 23.836 | 1859.208
610461 | Project A | Area4 | Sub Area 41 | Section 411 | C-10308 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6017 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610461 | Project A | Area4 | Sub Area 41 | Section 411 | C-10308 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610462 | Project A | Area4 | Sub Area 41 | Section 411 | C-10309 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8pr16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.19079 | 4.7697 | IWP-6028 | 0.8 | 0 | 3.8157 | 78 | 0 | 297.6276 | 3.8157 | 297.6276
610462 | Project A | Area4 | Sub Area 41 | Section 411 | C-10309 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6017 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610462 | Project A | Area4 | Sub Area 41 | Section 411 | C-10309 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6028 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610463 | Project A | Area4 | Sub Area 41 | Section 411 | C-10310 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable4triad 16awg Shld 300V ACIC, Random Fill | M | 25 | 1 | Tray | 0.1946 | 4.8651 | IWP-6028 | 0.8 | 0 | 3.8921 | 78 | 0 | 303.5801 | 3.8921 | 303.5801
610463 | Project A | Area4 | Sub Area 41 | Section 411 | C-10310 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6017 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610463 | Project A | Area4 | Sub Area 41 | Section 411 | C-10310 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6028 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610464 | Project A | Area4 | Sub Area 41 | Section 411 | C-10311 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.22572 | 5.643 | IWP-6028 | 0.8 | 0 | 4.5144 | 78 | 0 | 352.1227 | 4.5144 | 352.1227
610464 | Project A | Area4 | Sub Area 41 | Section 411 | C-10311 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6017 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610464 | Project A | Area4 | Sub Area 41 | Section 411 | C-10311 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6028 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610465 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10003 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6028 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610465 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10003 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6020 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610465 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10003 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6020 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610466 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10004 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6028 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610466 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10004 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6020 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610466 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10004 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6020 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610467 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10005 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6028 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610467 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10005 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6020 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610467 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10005 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6020 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610468 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10006 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6028 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610468 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10006 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6020 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610468 | Project A | Area4 | Sub Area 41 | Section 411 | CAT-10006 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6020 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610469 | Project A | Area4 | Sub Area 41 | Section 411 | C-10312 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable10c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.16929 | 0.84645 | IWP-6028 | 0.75 | 0.63484 | 0 | 110 | 69.832 | 0 | 0.63484 | 69.832
610469 | Project A | Area4 | Sub Area 41 | Section 411 | C-10312 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6020 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610469 | Project A | Area4 | Sub Area 41 | Section 411 | C-10312 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6028 | 0.75 | 1.98 | 0 | 110 | 217.8 | 0 | 1.98 | 217.8
610470 | Project A | Area4 | Sub Area 41 | Section 411 | C-10313 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12988 | 0.64939 | IWP-6028 | 0.75 | 0.48704 | 0 | 110 | 53.5748 | 0 | 0.48704 | 53.5748
610470 | Project A | Area4 | Sub Area 41 | Section 411 | C-10313 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610470 | Project A | Area4 | Sub Area 41 | Section 411 | C-10313 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6028 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610471 | Project A | Area4 | Sub Area 41 | Section 411 | C-10314 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 12 | 1 | Tray | 0.12988 | 1.5585 | IWP-6028 | 0.75 | 1.1689 | 0 | 110 | 128.5796 | 0 | 1.1689 | 128.5796
610471 | Project A | Area4 | Sub Area 41 | Section 411 | C-10314 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610471 | Project A | Area4 | Sub Area 41 | Section 411 | C-10314 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6028 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610472 | Project A | Area4 | Sub Area 41 | Section 411 | C-10315 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12988 | 1.9482 | IWP-6028 | 0.75 | 1.4611 | 0 | 110 | 160.7245 | 0 | 1.4611 | 160.7245
610472 | Project A | Area4 | Sub Area 41 | Section 411 | C-10315 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610472 | Project A | Area4 | Sub Area 41 | Section 411 | C-10315 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6028 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610473 | Project A | Area4 | Sub Area 41 | Section 411 | C-10316 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6028 | 0.75 | 2.4352 | 0 | 110 | 267.8742 | 0 | 2.4352 | 267.8742
610473 | Project A | Area4 | Sub Area 41 | Section 411 | C-10316 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610473 | Project A | Area4 | Sub Area 41 | Section 411 | C-10316 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6028 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610474 | Project A | Area4 | Sub Area 41 | Section 411 | C-10317 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 10 | 1 | Tray | 0.095393 | 0.95393 | IWP-6028 | 0.75 | 0.71545 | 0 | 110 | 78.6996 | 0 | 0.71545 | 78.6996
610474 | Project A | Area4 | Sub Area 41 | Section 411 | C-10317 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610474 | Project A | Area4 | Sub Area 41 | Section 411 | C-10317 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6028 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610475 | Project A | Area4 | Sub Area 41 | Section 411 | C-10318 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 5 | 1 | Tray | 0.095393 | 0.47697 | IWP-6028 | 0.75 | 0.35773 | 0 | 110 | 39.3498 | 0 | 0.35773 | 39.3498
610475 | Project A | Area4 | Sub Area 41 | Section 411 | C-10318 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610475 | Project A | Area4 | Sub Area 41 | Section 411 | C-10318 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6028 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610476 | Project A | Area4 | Sub Area 41 | Section 411 | C-10319 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable1pr16awg Shld 300V ACIC, Random Fill | M | 15 | 1 | Tray | 0.095393 | 1.4309 | IWP-6029 | 0.75 | 1.0732 | 0 | 110 | 118.0494 | 0 | 1.0732 | 118.0494
610476 | Project A | Area4 | Sub Area 41 | Section 411 | C-10319 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610476 | Project A | Area4 | Sub Area 41 | Section 411 | C-10319 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6028 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610477 | Project A | Area4 | Sub Area 42 | Section 412 | C-10320 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610477 | Project A | Area4 | Sub Area 42 | Section 412 | C-10320 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6029 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610477 | Project A | Area4 | Sub Area 42 | Section 412 | C-10320 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610478 | Project A | Area4 | Sub Area 42 | Section 412 | C-10321 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 11 | 1 | Tray | 0.12316 | 1.3548 | IWP-6029 | 0.75 | 1.0161 | 0 | 110 | 111.7682 | 0 | 1.0161 | 111.7682
610478 | Project A | Area4 | Sub Area 42 | Section 412 | C-10321 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610478 | Project A | Area4 | Sub Area 42 | Section 412 | C-10321 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610479 | Project A | Area4 | Sub Area 42 | Section 412 | C-10322 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 11 | 1 | Tray | 0.12316 | 1.3548 | IWP-6029 | 0.75 | 1.0161 | 0 | 110 | 111.7682 | 0 | 1.0161 | 111.7682
610479 | Project A | Area4 | Sub Area 42 | Section 412 | C-10322 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610479 | Project A | Area4 | Sub Area 42 | Section 412 | C-10322 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610480 | Project A | Area4 | Sub Area 42 | Section 412 | C-10323 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 11 | 1 | Tray | 0.12316 | 1.3548 | IWP-6029 | 0.75 | 1.0161 | 0 | 110 | 111.7682 | 0 | 1.0161 | 111.7682
610480 | Project A | Area4 | Sub Area 42 | Section 412 | C-10323 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610480 | Project A | Area4 | Sub Area 42 | Section 412 | C-10323 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610481 | Project A | Area4 | Sub Area 42 | Section 412 | C-10324 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6029 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610481 | Project A | Area4 | Sub Area 42 | Section 412 | C-10324 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610481 | Project A | Area4 | Sub Area 42 | Section 412 | C-10324 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610482 | Project A | Area4 | Sub Area 42 | Section 412 | C-10325 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12316 | 1.8474 | IWP-6029 | 0.75 | 1.3856 | 0 | 110 | 152.4111 | 0 | 1.3856 | 152.4111
610482 | Project A | Area4 | Sub Area 42 | Section 412 | C-10325 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610482 | Project A | Area4 | Sub Area 42 | Section 412 | C-10325 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610483 | Project A | Area4 | Sub Area 42 | Section 412 | C-10326 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 16 | 1 | Tray | 0.12316 | 1.9706 | IWP-6029 | 0.75 | 1.4779 | 0 | 110 | 162.5719 | 0 | 1.4779 | 162.5719
610483 | Project A | Area4 | Sub Area 42 | Section 412 | C-10326 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610483 | Project A | Area4 | Sub Area 42 | Section 412 | C-10326 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610484 | Project A | Area4 | Sub Area 42 | Section 412 | C-10327 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12316 | 3.079 | IWP-6029 | 0.75 | 2.3093 | 0 | 110 | 254.0185 | 0 | 2.3093 | 254.0185
610484 | Project A | Area4 | Sub Area 42 | Section 412 | C-10327 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610484 | Project A | Area4 | Sub Area 42 | Section 412 | C-10327 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610485 | Project A | Area4 | Sub Area 42 | Section 412 | C-10328 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable20c14awg Cu 600V TECK, Random Fill | M | 333 | 1 | Tray | 0.22572 | 75.1647 | IWP-6029 | 0.8 | 0 | 60.1317 | 78 | 0 | 4690.2748 | 60.1317 | 4690.2748
610485 | Project A | Area4 | Sub Area 42 | Section 412 | C-10328 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6017 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610485 | Project A | Area4 | Sub Area 42 | Section 412 | C-10328 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 40 | 1 |  | 0.132 | 5.28 | IWP-6029 | 0.8 | 0 | 4.224 | 78 | 0 | 329.472 | 4.224 | 329.472
610486 | Project A | Area4 | Sub Area 42 | Section 412 | C-10329 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 23 | 1 | Tray | 0.13257 | 3.049 | IWP-6029 | 0.8 | 0 | 2.4392 | 78 | 0 | 190.258 | 2.4392 | 190.258
610486 | Project A | Area4 | Sub Area 42 | Section 412 | C-10329 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610486 | Project A | Area4 | Sub Area 42 | Section 412 | C-10329 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6029 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610487 | Project A | Area4 | Sub Area 42 | Section 412 | C-10330 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 30 | 1 | Tray | 0.13257 | 3.977 | IWP-6029 | 0.8 | 0 | 3.1816 | 78 | 0 | 248.1626 | 3.1816 | 248.1626
610487 | Project A | Area4 | Sub Area 42 | Section 412 | C-10330 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610487 | Project A | Area4 | Sub Area 42 | Section 412 | C-10330 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6029 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610488 | Project A | Area4 | Sub Area 42 | Section 412 | C-10331 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 13 | 1 | Tray | 0.13257 | 1.7234 | IWP-6029 | 0.8 | 0 | 1.3787 | 78 | 0 | 107.5371 | 1.3787 | 107.5371
610488 | Project A | Area4 | Sub Area 42 | Section 412 | C-10331 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610488 | Project A | Area4 | Sub Area 42 | Section 412 | C-10331 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6029 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610489 | Project A | Area4 | Sub Area 42 | Section 412 | C-10332 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 30 | 1 | Tray | 0.13257 | 3.977 | IWP-6029 | 0.8 | 0 | 3.1816 | 78 | 0 | 248.1626 | 3.1816 | 248.1626
610489 | Project A | Area4 | Sub Area 42 | Section 412 | C-10332 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610489 | Project A | Area4 | Sub Area 42 | Section 412 | C-10332 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6029 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610490 | Project A | Area4 | Sub Area 42 | Section 412 | C-10333 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.13257 | 3.3141 | IWP-6029 | 0.8 | 0 | 2.6513 | 78 | 0 | 206.8022 | 2.6513 | 206.8022
610490 | Project A | Area4 | Sub Area 42 | Section 412 | C-10333 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610490 | Project A | Area4 | Sub Area 42 | Section 412 | C-10333 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6029 | 0.8 | 0 | 1.2672 | 78 | 0 | 98.8416 | 1.2672 | 98.8416
610491 | Project A | Area4 | Sub Area 42 | Section 412 | C-10334 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable10c14awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.16929 | 1.6929 | IWP-6029 | 0.8 | 0 | 1.3543 | 78 | 0 | 105.6368 | 1.3543 | 105.6368
610491 | Project A | Area4 | Sub Area 42 | Section 412 | C-10334 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6017 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610491 | Project A | Area4 | Sub Area 42 | Section 412 | C-10334 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6029 | 0.8 | 0 | 2.112 | 78 | 0 | 164.736 | 2.112 | 164.736
610492 | Project A | Area4 | Sub Area 42 | Section 412 | C-10335 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable10c14awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.16929 | 1.6929 | IWP-6029 | 0.8 | 0 | 1.3543 | 78 | 0 | 105.6368 | 1.3543 | 105.6368
610492 | Project A | Area4 | Sub Area 42 | Section 412 | C-10335 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6017 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610492 | Project A | Area4 | Sub Area 42 | Section 412 | C-10335 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6029 | 0.8 | 0 | 2.112 | 78 | 0 | 164.736 | 2.112 | 164.736
610493 | Project A | Area4 | Sub Area 42 | Section 412 | C-10336 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 47 | 1 | Tray | 0.12988 | 6.1043 | IWP-6029 | 0.8 | 0 | 4.8834 | 78 | 0 | 380.9074 | 4.8834 | 380.9074
610493 | Project A | Area4 | Sub Area 42 | Section 412 | C-10336 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610493 | Project A | Area4 | Sub Area 42 | Section 412 | C-10336 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6029 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610494 | Project A | Area4 | Sub Area 42 | Section 412 | C-10337 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 14 | 1 | Tray | 0.12988 | 1.8183 | IWP-6029 | 0.8 | 0 | 1.4546 | 78 | 0 | 113.4618 | 1.4546 | 113.4618
610494 | Project A | Area4 | Sub Area 42 | Section 412 | C-10337 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610494 | Project A | Area4 | Sub Area 42 | Section 412 | C-10337 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6029 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610495 | Project A | Area4 | Sub Area 42 | Section 412 | C-10338 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 23 | 1 | Tray | 0.12988 | 2.9872 | IWP-6029 | 0.8 | 0 | 2.3898 | 78 | 0 | 186.4015 | 2.3898 | 186.4015
610495 | Project A | Area4 | Sub Area 42 | Section 412 | C-10338 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610495 | Project A | Area4 | Sub Area 42 | Section 412 | C-10338 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6029 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610496 | Project A | Area4 | Sub Area 42 | Section 412 | C-10339 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 18 | 1 | Tray | 0.12988 | 2.3378 | IWP-6029 | 0.8 | 0 | 1.8702 | 78 | 0 | 145.8794 | 1.8702 | 145.8794
610496 | Project A | Area4 | Sub Area 42 | Section 412 | C-10339 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610496 | Project A | Area4 | Sub Area 42 | Section 412 | C-10339 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6029 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610497 | Project A | Area4 | Sub Area 42 | Section 412 | C-10340 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12988 | 3.247 | IWP-6029 | 0.8 | 0 | 2.5976 | 78 | 0 | 202.6103 | 2.5976 | 202.6103
610497 | Project A | Area4 | Sub Area 42 | Section 412 | C-10340 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6017 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610497 | Project A | Area4 | Sub Area 42 | Section 412 | C-10340 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6029 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610498 | Project A | Area4 | Sub Area 42 | Section 412 | CAT-10007 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | NA | Module | Install Tray CableCat6e | M | 25 | 1 | Tray | 0 | 0 | IWP-6029 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610499 | Project A | Area4 | Sub Area 42 | Section 412 | C-10341 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg, Unarmored | M | 31 | 1 | Tray | 0.095393 | 2.9572 | IWP-6029 | 0.8 | 0 | 2.3658 | 78 | 0 | 184.5291 | 2.3658 | 184.5291
610499 | Project A | Area4 | Sub Area 42 | Section 412 | C-10341 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.5304 | 1.0608 | IWP-6017 | 0.8 | 0 | 0.84864 | 78 | 0 | 66.1939 | 0.84864 | 66.1939
610499 | Project A | Area4 | Sub Area 42 | Section 412 | C-10341 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610500 | Project A | Area4 | Sub Area 42 | Section 412 | C-10342 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg, Unarmored | M | 31 | 1 | Tray | 0.095393 | 2.9572 | IWP-6029 | 0.8 | 0 | 2.3658 | 78 | 0 | 184.5291 | 2.3658 | 184.5291
610500 | Project A | Area4 | Sub Area 42 | Section 412 | C-10342 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.5304 | 1.0608 | IWP-6017 | 0.8 | 0 | 0.84864 | 78 | 0 | 66.1939 | 0.84864 | 66.1939
610500 | Project A | Area4 | Sub Area 42 | Section 412 | C-10342 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610501 | Project A | Area4 | Sub Area 42 | Section 412 | C-10343 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg, Unarmored | M | 55 | 1 | Tray | 0.095393 | 5.2466 | IWP-6029 | 0.8 | 0 | 4.1973 | 78 | 0 | 327.3903 | 4.1973 | 327.3903
610501 | Project A | Area4 | Sub Area 42 | Section 412 | C-10343 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.5304 | 1.0608 | IWP-6017 | 0.8 | 0 | 0.84864 | 78 | 0 | 66.1939 | 0.84864 | 66.1939
610501 | Project A | Area4 | Sub Area 42 | Section 412 | C-10343 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610502 | Project A | Area4 | Sub Area 42 | Section 412 | C-10344 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable1pr16awg, Unarmored | M | 14 | 1 | Tray | 0.095393 | 1.3355 | IWP-6029 | 0.8 | 0 | 1.0684 | 78 | 0 | 83.3357 | 1.0684 | 83.3357
610502 | Project A | Area4 | Sub Area 42 | Section 412 | C-10344 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.5304 | 1.0608 | IWP-6017 | 0.8 | 0 | 0.84864 | 78 | 0 | 66.1939 | 0.84864 | 66.1939
610502 | Project A | Area4 | Sub Area 42 | Section 412 | C-10344 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6029 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610503 | Project A | Area4 | Sub Area 42 | Section 412 | C-10345 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable10c14awg | M | 5 | 1 | Tray | 0.16929 | 0.84645 | IWP-6029 | 0.75 | 0.63484 | 0 | 110 | 69.832 | 0 | 0.63484 | 69.832
610503 | Project A | Area4 | Sub Area 42 | Section 412 | C-10345 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6020 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610503 | Project A | Area4 | Sub Area 42 | Section 412 | C-10345 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6029 | 0.75 | 1.98 | 0 | 110 | 217.8 | 0 | 1.98 | 217.8
610504 | Project A | Area4 | Sub Area 42 | Section 412 | C-10346 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable10c14awg | M | 5 | 1 | Tray | 0.16929 | 0.84645 | IWP-6029 | 0.75 | 0.63484 | 0 | 110 | 69.832 | 0 | 0.63484 | 69.832
610504 | Project A | Area4 | Sub Area 42 | Section 412 | C-10346 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6020 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610504 | Project A | Area4 | Sub Area 42 | Section 412 | C-10346 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6029 | 0.75 | 1.98 | 0 | 110 | 217.8 | 0 | 1.98 | 217.8
610505 | Project A | Area4 | Sub Area 42 | Section 412 | C-10347 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable10c14awg | M | 5 | 1 | Tray | 0.16929 | 0.84645 | IWP-6029 | 0.75 | 0.63484 | 0 | 110 | 69.832 | 0 | 0.63484 | 69.832
610505 | Project A | Area4 | Sub Area 42 | Section 412 | C-10347 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6020 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610505 | Project A | Area4 | Sub Area 42 | Section 412 | C-10347 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6029 | 0.75 | 1.98 | 0 | 110 | 217.8 | 0 | 1.98 | 217.8
610506 | Project A | Area4 | Sub Area 42 | Section 412 | C-10348 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable10c14awg | M | 5 | 1 | Tray | 0.16929 | 0.84645 | IWP-6029 | 0.75 | 0.63484 | 0 | 110 | 69.832 | 0 | 0.63484 | 69.832
610506 | Project A | Area4 | Sub Area 42 | Section 412 | C-10348 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6020 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610506 | Project A | Area4 | Sub Area 42 | Section 412 | C-10348 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 20 | 1 |  | 0.132 | 2.64 | IWP-6029 | 0.75 | 1.98 | 0 | 110 | 217.8 | 0 | 1.98 | 217.8
610507 | Project A | Area4 | Sub Area 42 | Section 412 | B-10006 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2004 | 2004 - AWG 12 to AWG 3 | 16122202004 | 16122202004 - MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | Cable | 5kV | Field | Install DirBuried Cable6awg | M | 38 | 1 | DirBuried | 0.14897 | 5.661 | IWP-6029 | 0.8 | 0 | 4.5288 | 78 | 0 | 353.2495 | 4.5288 | 353.2495
610507 | Project A | Area4 | Sub Area 42 | Section 412 | B-10006 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2004 | 2004 - AWG 12 to AWG 3 | 16142202004 | 16142202004 - Terminations - MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 0.14897 | 0.89385 | IWP-6029 | 0.8 | 0 | 0.71508 | 78 | 0 | 55.7762 | 0.71508 | 55.7762
610507 | Project A | Area4 | Sub Area 42 | Section 412 | B-10006 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2004 | 2004 - AWG 12 to AWG 3 | 16132202004 | 16132202004 - Connectors - MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6008 | 0.8 | 0 | 3.3072 | 78 | 0 | 257.9616 | 3.3072 | 257.9616
610508 | Project A | Area4 | Sub Area 42 | Section 412 | B-10007 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install DirBuried Cable500mcm Cu 5kV Unshld TECK 90C | M | 38 | 1 | DirBuried | 0.33519 | 12.7374 | IWP-6029 | 0.8 | 0 | 10.1899 | 78 | 0 | 794.8113 | 10.1899 | 794.8113
610508 | Project A | Area4 | Sub Area 42 | Section 412 | B-10007 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6029 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610508 | Project A | Area4 | Sub Area 42 | Section 412 | B-10007 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6008 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610509 | Project A | Area4 | Sub Area 42 | Section 412 | B-10008 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install DirBuried Cable500mcm Cu 5kV Unshld TECK 90C | M | 38 | 1 | DirBuried | 0.33519 | 12.7374 | IWP-6029 | 0.8 | 0 | 10.1899 | 78 | 0 | 794.8113 | 10.1899 | 794.8113
610509 | Project A | Area4 | Sub Area 42 | Section 412 | B-10008 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6029 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610509 | Project A | Area4 | Sub Area 42 | Section 412 | B-10008 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6008 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610510 | Project A | Area4 | Sub Area 42 | Section 412 | B-10009 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install DirBuried Cable500mcm Cu 5kV Unshld TECK 90C | M | 38 | 1 | DirBuried | 0.33519 | 12.7374 | IWP-6029 | 0.8 | 0 | 10.1899 | 78 | 0 | 794.8113 | 10.1899 | 794.8113
610510 | Project A | Area4 | Sub Area 42 | Section 412 | B-10009 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6029 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610510 | Project A | Area4 | Sub Area 42 | Section 412 | B-10009 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6008 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610511 | Project A | Area4 | Sub Area 42 | Section 412 | B-10010 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install DirBuried Cable500mcm Cu 5kV Unshld TECK 90C | M | 38 | 1 | DirBuried | 0.33519 | 12.7374 | IWP-6029 | 0.8 | 0 | 10.1899 | 78 | 0 | 794.8113 | 10.1899 | 794.8113
610511 | Project A | Area4 | Sub Area 42 | Section 412 | B-10010 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6029 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610511 | Project A | Area4 | Sub Area 42 | Section 412 | B-10010 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6008 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610512 | Project A | Area4 | Sub Area 42 | Section 412 | B-10011 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install DirBuried Cable500mcm Cu 5kV Unshld TECK 90C | M | 38 | 1 | DirBuried | 0.33519 | 12.7374 | IWP-6030 | 0.8 | 0 | 10.1899 | 78 | 0 | 794.8113 | 10.1899 | 794.8113
610512 | Project A | Area4 | Sub Area 42 | Section 412 | B-10011 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6029 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610512 | Project A | Area4 | Sub Area 42 | Section 412 | B-10011 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6008 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610513 | Project A | Area4 | Sub Area 42 | Section 412 | B-10012 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install DirBuried Cable500mcm Cu 5kV Unshld TECK 90C | M | 38 | 1 | DirBuried | 0.33519 | 12.7374 | IWP-6030 | 0.8 | 0 | 10.1899 | 78 | 0 | 794.8113 | 10.1899 | 794.8113
610513 | Project A | Area4 | Sub Area 42 | Section 412 | B-10012 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6030 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610513 | Project A | Area4 | Sub Area 42 | Section 412 | B-10012 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6008 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610514 | Project A | Area4 | Sub Area 42 | Section 412 | C-10350 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable6awg Cu 1kV TECK, Random Fill | M | 25 | 1 | Tray | 0.18228 | 4.5569 | IWP-6030 | 0.8 | 0 | 3.6456 | 78 | 0 | 284.3531 | 3.6456 | 284.3531
610514 | Project A | Area4 | Sub Area 42 | Section 412 | C-10350 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 1.4625 | 2.925 | IWP-6017 | 0.8 | 0 | 2.34 | 78 | 0 | 182.52 | 2.34 | 182.52
610514 | Project A | Area4 | Sub Area 42 | Section 412 | C-10350 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 4 | 1 |  | 0.26 | 1.04 | IWP-6030 | 0.8 | 0 | 0.832 | 78 | 0 | 64.896 | 0.832 | 64.896
610515 | Project A | Area4 | Sub Area 42 | Section 412 | P-10155 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16122302002 | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Cable | 1kV | Field | Install Tray Cable250mcm Cu 1kV TECK | M | 15 | 1 | Tray | 0.37799 | 5.6699 | IWP-6030 | 0.8 | 0 | 4.5359 | 78 | 0 | 353.7995 | 4.5359 | 353.7995
610515 | Project A | Area4 | Sub Area 42 | Section 412 | P-10155 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16132302002 | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6017 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610515 | Project A | Area4 | Sub Area 42 | Section 412 | P-10155 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16142302002 | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.65 | 3.9 | IWP-6030 | 0.8 | 0 | 3.12 | 78 | 0 | 243.36 | 3.12 | 243.36
610516 | Project A | Area4 | Sub Area 42 | Section 412 | P-10156 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16122302002 | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Cable | 1kV | Field | Install Tray Cable250mcm Cu 1kV TECK | M | 15 | 1 | Tray | 0.37799 | 5.6699 | IWP-6030 | 0.8 | 0 | 4.5359 | 78 | 0 | 353.7995 | 4.5359 | 353.7995
610516 | Project A | Area4 | Sub Area 42 | Section 412 | P-10156 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16132302002 | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6017 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610516 | Project A | Area4 | Sub Area 42 | Section 412 | P-10156 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16142302002 | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.65 | 3.9 | IWP-6030 | 0.8 | 0 | 3.12 | 78 | 0 | 243.36 | 3.12 | 243.36
610517 | Project A | Area4 | Sub Area 42 | Section 412 | P-10157 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16122302002 | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Cable | 1kV | Field | Install Tray Cable250mcm Cu 1kV TECK | M | 15 | 1 | Tray | 0.37799 | 5.6699 | IWP-6030 | 0.8 | 0 | 4.5359 | 78 | 0 | 353.7995 | 4.5359 | 353.7995
610517 | Project A | Area4 | Sub Area 42 | Section 412 | P-10157 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16132302002 | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.808 | 5.616 | IWP-6017 | 0.8 | 0 | 4.4928 | 78 | 0 | 350.4384 | 4.4928 | 350.4384
610517 | Project A | Area4 | Sub Area 42 | Section 412 | P-10157 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16142302002 | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Terminations | 1kV | Field | 1kV Terminations | EA | 6 | 1 |  | 0.65 | 3.9 | IWP-6030 | 0.8 | 0 | 3.12 | 78 | 0 | 243.36 | 3.12 | 243.36
610518 | Project A | Area4 | Sub Area 42 | Section 412 | P-10158 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16122302002 | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Cable | 1kV | Module | Install Tray Cable300mcm Cu 1kV CONDUIT, Random Fill | M | 5 | 1 | Tray | 0.45726 | 2.2863 | IWP-6030 | 0.75 | 1.7147 | 0 | 110 | 188.6204 | 0 | 1.7147 | 188.6204
610518 | Project A | Area4 | Sub Area 42 | Section 412 | P-10158 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16132302002 | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 3.666 | 7.332 | IWP-6020 | 0.75 | 5.499 | 0 | 110 | 604.89 | 0 | 5.499 | 604.89
610518 | Project A | Area4 | Sub Area 42 | Section 412 | P-10158 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16142302002 | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Terminations | 1kV | Module | 1kV Terminations | EA | 8 | 1 |  | 0.715 | 5.72 | IWP-6030 | 0.75 | 4.29 | 0 | 110 | 471.9 | 0 | 4.29 | 471.9
610519 | Project A | Area4 | Sub Area 42 | Section 412 | P-10159 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16122302002 | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Cable | 1kV | Module | Install Tray Cable300mcm Cu 1kV CONDUIT, Random Fill | M | 5 | 1 | Tray | 0.45726 | 2.2863 | IWP-6030 | 0.75 | 1.7147 | 0 | 110 | 188.6204 | 0 | 1.7147 | 188.6204
610519 | Project A | Area4 | Sub Area 42 | Section 412 | P-10159 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16132302002 | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 3.666 | 7.332 | IWP-6020 | 0.75 | 5.499 | 0 | 110 | 604.89 | 0 | 5.499 | 604.89
610519 | Project A | Area4 | Sub Area 42 | Section 412 | P-10159 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2002 | 2002 - 250 mcm to 500 mcm | 16142302002 | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Terminations | 1kV | Module | 1kV Terminations | EA | 8 | 1 |  | 0.715 | 5.72 | IWP-6030 | 0.75 | 4.29 | 0 | 110 | 471.9 | 0 | 4.29 | 471.9
610520 | Project A | Area4 | Sub Area 42 | Section 412 | C-10351 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610520 | Project A | Area4 | Sub Area 42 | Section 412 | C-10351 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6030 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610520 | Project A | Area4 | Sub Area 42 | Section 412 | C-10351 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610521 | Project A | Area4 | Sub Area 42 | Section 412 | C-10352 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610521 | Project A | Area4 | Sub Area 42 | Section 412 | C-10352 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6030 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610521 | Project A | Area4 | Sub Area 42 | Section 412 | C-10352 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610522 | Project A | Area4 | Sub Area 42 | Section 412 | C-10353 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610522 | Project A | Area4 | Sub Area 42 | Section 412 | C-10353 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6030 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610522 | Project A | Area4 | Sub Area 42 | Section 412 | C-10353 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610523 | Project A | Area4 | Sub Area 42 | Section 412 | C-10354 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610523 | Project A | Area4 | Sub Area 42 | Section 412 | C-10354 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6030 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610523 | Project A | Area4 | Sub Area 42 | Section 412 | C-10354 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610524 | Project A | Area4 | Sub Area 42 | Section 412 | P-10160 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 1kV | Field | Install Tray Cable8awg Cu 1kV TECK, Random Fill | M | 345 | 1 | Tray | 0.16257 | 56.0873 | IWP-6030 | 0.8 | 0 | 44.8698 | 78 | 0 | 3499.8479 | 44.8698 | 3499.8479
610524 | Project A | Area4 | Sub Area 42 | Section 412 | P-10160 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 1kV | Field | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6017 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610524 | Project A | Area4 | Sub Area 42 | Section 412 | P-10160 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 1kV | Field | 1kV Terminations | EA | 4 | 1 |  | 0.198 | 0.792 | IWP-6030 | 0.8 | 0 | 0.6336 | 78 | 0 | 49.4208 | 0.6336 | 49.4208
610525 | Project A | Area4 | Sub Area 42 | Section 412 | P-10161 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610525 | Project A | Area4 | Sub Area 42 | Section 412 | P-10161 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 28 | 1 | Tray | 0.12809 | 3.5864 | IWP-6030 | 0.75 | 2.6898 | 0 | 110 | 295.881 | 0 | 2.6898 | 295.881
610525 | Project A | Area4 | Sub Area 42 | Section 412 | P-10161 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610526 | Project A | Area4 | Sub Area 42 | Section 412 | P-10162 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 10 | 1 | Tray | 0.1469 | 1.469 | IWP-6030 | 0.75 | 1.1017 | 0 | 110 | 121.1899 | 0 | 1.1017 | 121.1899
610526 | Project A | Area4 | Sub Area 42 | Section 412 | P-10162 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610526 | Project A | Area4 | Sub Area 42 | Section 412 | P-10162 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.165 | 1.32 | IWP-6030 | 0.75 | 0.99 | 0 | 110 | 108.9 | 0 | 0.99 | 108.9
610527 | Project A | Area4 | Sub Area 42 | Section 412 | P-10163 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610527 | Project A | Area4 | Sub Area 42 | Section 412 | P-10163 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 12 | 1 | Tray | 0.12809 | 1.537 | IWP-6030 | 0.75 | 1.1528 | 0 | 110 | 126.8061 | 0 | 1.1528 | 126.8061
610527 | Project A | Area4 | Sub Area 42 | Section 412 | P-10163 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610528 | Project A | Area4 | Sub Area 42 | Section 412 | P-10164 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610528 | Project A | Area4 | Sub Area 42 | Section 412 | P-10164 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 15 | 1 | Tray | 0.12809 | 1.9213 | IWP-6030 | 0.75 | 1.441 | 0 | 110 | 158.5077 | 0 | 1.441 | 158.5077
610528 | Project A | Area4 | Sub Area 42 | Section 412 | P-10164 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6020 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610529 | Project A | Area4 | Sub Area 42 | Section 412 | P-10165 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610529 | Project A | Area4 | Sub Area 42 | Section 412 | P-10165 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 10 | 1 | Tray | 0.12809 | 1.2809 | IWP-6020 | 0.75 | 0.96065 | 0 | 110 | 105.6718 | 0 | 0.96065 | 105.6718
610529 | Project A | Area4 | Sub Area 42 | Section 412 | P-10165 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610530 | Project A | Area4 | Sub Area 42 | Section 412 | P-10166 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610530 | Project A | Area4 | Sub Area 42 | Section 412 | P-10166 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 11 | 1 | Tray | 0.12809 | 1.409 | IWP-6020 | 0.75 | 1.0567 | 0 | 110 | 116.239 | 0 | 1.0567 | 116.239
610530 | Project A | Area4 | Sub Area 42 | Section 412 | P-10166 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610531 | Project A | Area4 | Sub Area 42 | Section 412 | P-10167 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610531 | Project A | Area4 | Sub Area 42 | Section 412 | P-10167 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 12 | 1 | Tray | 0.12809 | 1.537 | IWP-6020 | 0.75 | 1.1528 | 0 | 110 | 126.8061 | 0 | 1.1528 | 126.8061
610531 | Project A | Area4 | Sub Area 42 | Section 412 | P-10167 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610532 | Project A | Area4 | Sub Area 42 | Section 412 | P-10168 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610532 | Project A | Area4 | Sub Area 42 | Section 412 | P-10168 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 10 | 1 | Tray | 0.12809 | 1.2809 | IWP-6020 | 0.75 | 0.96065 | 0 | 110 | 105.6718 | 0 | 0.96065 | 105.6718
610532 | Project A | Area4 | Sub Area 42 | Section 412 | P-10168 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610533 | Project A | Area4 | Sub Area 42 | Section 412 | P-10169 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg | M | 15 | 1 | Tray | 0.12809 | 1.9213 | IWP-6020 | 0.75 | 1.441 | 0 | 110 | 158.5077 | 0 | 1.441 | 158.5077
610533 | Project A | Area4 | Sub Area 42 | Section 412 | P-10169 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610533 | Project A | Area4 | Sub Area 42 | Section 412 | P-10169 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610534 | Project A | Area4 | Sub Area 42 | Section 412 | P-10170 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg CU 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.1469 | 0.73448 | IWP-6020 | 0.75 | 0.55086 | 0 | 110 | 60.595 | 0 | 0.55086 | 60.595
610534 | Project A | Area4 | Sub Area 42 | Section 412 | P-10170 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610534 | Project A | Area4 | Sub Area 42 | Section 412 | P-10170 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.165 | 1.32 | IWP-6030 | 0.75 | 0.99 | 0 | 110 | 108.9 | 0 | 0.99 | 108.9
610535 | Project A | Area4 | Sub Area 42 | Section 412 | P-10171 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable6c12awg Cu 600V TECK, Random Fill | M | 13 | 1 | Tray | 0.16123 | 2.096 | IWP-6020 | 0.75 | 1.572 | 0 | 110 | 172.9174 | 0 | 1.572 | 172.9174
610535 | Project A | Area4 | Sub Area 42 | Section 412 | P-10171 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610535 | Project A | Area4 | Sub Area 42 | Section 412 | P-10171 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.165 | 1.98 | IWP-6030 | 0.75 | 1.485 | 0 | 110 | 163.35 | 0 | 1.485 | 163.35
610536 | Project A | Area4 | Sub Area 42 | Section 412 | P-10172 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610536 | Project A | Area4 | Sub Area 42 | Section 412 | P-10172 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 16 | 1 | Tray | 0.12809 | 2.0494 | IWP-6020 | 0.75 | 1.537 | 0 | 110 | 169.0748 | 0 | 1.537 | 169.0748
610536 | Project A | Area4 | Sub Area 42 | Section 412 | P-10172 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610537 | Project A | Area4 | Sub Area 42 | Section 412 | P-10173 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610537 | Project A | Area4 | Sub Area 42 | Section 412 | P-10173 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 24 | 1 | Tray | 0.12809 | 3.0741 | IWP-6020 | 0.75 | 2.3056 | 0 | 110 | 253.6123 | 0 | 2.3056 | 253.6123
610537 | Project A | Area4 | Sub Area 42 | Section 412 | P-10173 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610538 | Project A | Area4 | Sub Area 42 | Section 412 | P-10174 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.165 | 0.66 | IWP-6030 | 0.75 | 0.495 | 0 | 110 | 54.45 | 0 | 0.495 | 54.45
610538 | Project A | Area4 | Sub Area 42 | Section 412 | P-10174 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Module | Install Tray Cable12awg Cu 600V TECK, Random Fill | M | 28 | 1 | Tray | 0.12809 | 3.5864 | IWP-6020 | 0.75 | 2.6898 | 0 | 110 | 295.881 | 0 | 2.6898 | 295.881
610538 | Project A | Area4 | Sub Area 42 | Section 412 | P-10174 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610539 | Project A | Area4 | Sub Area 42 | Section 412 | C-10355 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610539 | Project A | Area4 | Sub Area 42 | Section 412 | C-10355 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6020 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610539 | Project A | Area4 | Sub Area 42 | Section 412 | C-10355 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610540 | Project A | Area4 | Sub Area 42 | Section 412 | C-10356 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable6c14awg Cu 600V TECK, Random Fill | M | 10 | 1 | Tray | 0.13257 | 1.3257 | IWP-6020 | 0.75 | 0.99424 | 0 | 110 | 109.3665 | 0 | 0.99424 | 109.3665
610540 | Project A | Area4 | Sub Area 42 | Section 412 | C-10356 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610540 | Project A | Area4 | Sub Area 42 | Section 412 | C-10356 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 12 | 1 |  | 0.132 | 1.584 | IWP-6030 | 0.75 | 1.188 | 0 | 110 | 130.68 | 0 | 1.188 | 130.68
610541 | Project A | Area4 | Sub Area 42 | Section 412 | P-10175 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable1/0awg Cu 1kV TECK | M | 10 | 1 | Tray | 0.22001 | 2.2001 | IWP-6020 | 0.75 | 1.6501 | 0 | 110 | 181.5078 | 0 | 1.6501 | 181.5078
610541 | Project A | Area4 | Sub Area 42 | Section 412 | P-10175 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6030 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610541 | Project A | Area4 | Sub Area 42 | Section 412 | P-10175 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 2 | 1 |  | 0.429 | 0.858 | IWP-6030 | 0.75 | 0.6435 | 0 | 110 | 70.785 | 0 | 0.6435 | 70.785
610542 | Project A | Area4 | Sub Area 42 | Section 412 | CAT-10008 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 12 | 1 | Tray | 0.03281 | 0.39372 | IWP-6020 | 0.75 | 0.29529 | 0 | 110 | 32.4819 | 0 | 0.29529 | 32.4819
610542 | Project A | Area4 | Sub Area 42 | Section 412 | CAT-10008 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6030 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610542 | Project A | Area4 | Sub Area 42 | Section 412 | CAT-10008 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6030 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610543 | Project A | Area4 | Sub Area 43 | Section 413 | C-10357 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable30c14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.23692 | 1.1846 | IWP-6020 | 0.75 | 0.88844 | 0 | 110 | 97.7279 | 0 | 0.88844 | 97.7279
610543 | Project A | Area4 | Sub Area 43 | Section 413 | C-10357 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6030 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610543 | Project A | Area4 | Sub Area 43 | Section 413 | C-10357 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 60 | 1 |  | 0.132 | 7.92 | IWP-6030 | 0.75 | 5.94 | 0 | 110 | 653.4 | 0 | 5.94 | 653.4
610544 | Project A | Area4 | Sub Area 43 | Section 413 | C-10358 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610544 | Project A | Area4 | Sub Area 43 | Section 413 | C-10358 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6020 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610544 | Project A | Area4 | Sub Area 43 | Section 413 | C-10358 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610545 | Project A | Area4 | Sub Area 43 | Section 413 | P-10177 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable2awg Cu 1kV TECK, Random Fill | M | 5 | 1 | Tray | 0.18608 | 0.93042 | IWP-6020 | 0.75 | 0.69782 | 0 | 110 | 76.7598 | 0 | 0.69782 | 76.7598
610545 | Project A | Area4 | Sub Area 43 | Section 413 | P-10177 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610545 | Project A | Area4 | Sub Area 43 | Section 413 | P-10177 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 2 | 1 |  | 0.351 | 0.702 | IWP-6030 | 0.75 | 0.5265 | 0 | 110 | 57.915 | 0 | 0.5265 | 57.915
610546 | Project A | Area4 | Sub Area 43 | Section 413 | C-10359 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6020 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610546 | Project A | Area4 | Sub Area 43 | Section 413 | C-10359 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610546 | Project A | Area4 | Sub Area 43 | Section 413 | C-10359 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610547 | Project A | Area4 | Sub Area 43 | Section 413 | P-10178 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable2awg Cu 1kV TECK, Random Fill | M | 5 | 1 | Tray | 0.24811 | 1.2406 | IWP-6020 | 0.75 | 0.93042 | 0 | 110 | 102.3464 | 0 | 0.93042 | 102.3464
610547 | Project A | Area4 | Sub Area 43 | Section 413 | P-10178 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6030 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610547 | Project A | Area4 | Sub Area 43 | Section 413 | P-10178 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 6 | 1 |  | 0.351 | 2.106 | IWP-6030 | 0.75 | 1.5795 | 0 | 110 | 173.745 | 0 | 1.5795 | 173.745
610548 | Project A | Area4 | Sub Area 43 | Section 413 | P-10179 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16122302003 | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Cable | 1kV | Module | Install Tray Cable2awg Cu 1kV TECK, Random Fill | M | 5 | 1 | Tray | 0.18608 | 0.93042 | IWP-6020 | 0.75 | 0.69782 | 0 | 110 | 76.7598 | 0 | 0.69782 | 76.7598
610548 | Project A | Area4 | Sub Area 43 | Section 413 | P-10179 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16132302003 | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Connector | 1kV | Module | Install 1kV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610548 | Project A | Area4 | Sub Area 43 | Section 413 | P-10179 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2003 | 2003 - AWG 1/0 to AWG 2 | 16142302003 | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Terminations | 1kV | Module | 1kV Terminations | EA | 2 | 1 |  | 0.351 | 0.702 | IWP-6030 | 0.75 | 0.5265 | 0 | 110 | 57.915 | 0 | 0.5265 | 57.915
610549 | Project A | Area4 | Sub Area 43 | Section 413 | C-10360 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12316 | 1.8474 | IWP-6020 | 0.75 | 1.3856 | 0 | 110 | 152.4111 | 0 | 1.3856 | 152.4111
610549 | Project A | Area4 | Sub Area 43 | Section 413 | C-10360 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610549 | Project A | Area4 | Sub Area 43 | Section 413 | C-10360 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610550 | Project A | Area4 | Sub Area 43 | Section 413 | C-10361 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 95 | 1 | Tray | 0.12988 | 12.3384 | IWP-6017 | 0.8 | 0 | 9.8708 | 78 | 0 | 769.9192 | 9.8708 | 769.9192
610550 | Project A | Area4 | Sub Area 43 | Section 413 | C-10361 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610550 | Project A | Area4 | Sub Area 43 | Section 413 | C-10361 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6030 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610551 | Project A | Area4 | Sub Area 43 | Section 413 | C-10362 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 138 | 1 | Tray | 0.1946 | 26.8552 | IWP-6017 | 0.8 | 0 | 21.4841 | 78 | 0 | 1675.7619 | 21.4841 | 1675.7619
610551 | Project A | Area4 | Sub Area 43 | Section 413 | C-10362 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6030 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610551 | Project A | Area4 | Sub Area 43 | Section 413 | C-10362 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6030 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610552 | Project A | Area4 | Sub Area 43 | Section 413 | C-10363 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 138 | 1 | Tray | 0.1946 | 26.8552 | IWP-6017 | 0.8 | 0 | 21.4841 | 78 | 0 | 1675.7619 | 21.4841 | 1675.7619
610552 | Project A | Area4 | Sub Area 43 | Section 413 | C-10363 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6030 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610552 | Project A | Area4 | Sub Area 43 | Section 413 | C-10363 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6030 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610553 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10009 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | NA | Module | Install Tray CableCat6e | M | 18 | 1 | Tray | 0 | 0 | IWP-6020 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610554 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10010 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 18 | 1 | Tray | 0.03281 | 0.59058 | IWP-6020 | 0.75 | 0.44293 | 0 | 110 | 48.7228 | 0 | 0.44293 | 48.7228
610554 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10010 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6030 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610554 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10010 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6030 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610555 | Project A | Area4 | Sub Area 43 | Section 413 | C-10364 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg | M | 14 | 1 | Tray | 0.12988 | 1.8183 | IWP-6020 | 0.75 | 1.3637 | 0 | 110 | 150.0096 | 0 | 1.3637 | 150.0096
610555 | Project A | Area4 | Sub Area 43 | Section 413 | C-10364 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610555 | Project A | Area4 | Sub Area 43 | Section 413 | C-10364 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6030 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610556 | Project A | Area4 | Sub Area 43 | Section 413 | C-10365 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 14 | 1 | Tray | 0.12988 | 1.8183 | IWP-6020 | 0.75 | 1.3637 | 0 | 110 | 150.0096 | 0 | 1.3637 | 150.0096
610556 | Project A | Area4 | Sub Area 43 | Section 413 | C-10365 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610556 | Project A | Area4 | Sub Area 43 | Section 413 | C-10365 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6030 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610557 | Project A | Area4 | Sub Area 43 | Section 413 | C-10366 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 17 | 1 | Tray | 0.14331 | 2.4363 | IWP-6020 | 0.75 | 1.8273 | 0 | 110 | 200.998 | 0 | 1.8273 | 200.998
610557 | Project A | Area4 | Sub Area 43 | Section 413 | C-10366 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6030 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610557 | Project A | Area4 | Sub Area 43 | Section 413 | C-10366 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6030 | 0.75 | 1.584 | 0 | 110 | 174.24 | 0 | 1.584 | 174.24
610558 | Project A | Area4 | Sub Area 43 | Section 413 | C-10367 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable40c14awg Cu 600V TECK, Random Fill | M | 17 | 1 | Tray | 0.24811 | 4.2179 | IWP-6020 | 0.75 | 3.1634 | 0 | 110 | 347.9778 | 0 | 3.1634 | 347.9778
610558 | Project A | Area4 | Sub Area 43 | Section 413 | C-10367 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6030 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610558 | Project A | Area4 | Sub Area 43 | Section 413 | C-10367 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 80 | 1 |  | 0.132 | 10.56 | IWP-6030 | 0.75 | 7.92 | 0 | 110 | 871.2 | 0 | 7.92 | 871.2
610559 | Project A | Area4 | Sub Area 43 | Section 413 | P-10182 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install Tray Cable500mcm Cu 5kV Unshld TECK 90C | M | 85 | 1 | Tray | 0.53205 | 45.2245 | IWP-6017 | 0.8 | 0 | 36.1796 | 78 | 0 | 2822.0118 | 36.1796 | 2822.0118
610559 | Project A | Area4 | Sub Area 43 | Section 413 | P-10182 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6030 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610559 | Project A | Area4 | Sub Area 43 | Section 413 | P-10182 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6030 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610560 | Project A | Area4 | Sub Area 43 | Section 413 | P-10183 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.15809 | 12.6475 | IWP-6017 | 0.8 | 0 | 10.118 | 78 | 0 | 789.2018 | 10.118 | 789.2018
610560 | Project A | Area4 | Sub Area 43 | Section 413 | P-10183 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610560 | Project A | Area4 | Sub Area 43 | Section 413 | P-10183 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6030 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610561 | Project A | Area4 | Sub Area 43 | Section 413 | C-10368 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6020 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610561 | Project A | Area4 | Sub Area 43 | Section 413 | C-10368 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610561 | Project A | Area4 | Sub Area 43 | Section 413 | C-10368 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6030 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610562 | Project A | Area4 | Sub Area 43 | Section 413 | C-10369 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 120 | 1 | Tray | 0.12988 | 15.5854 | IWP-6017 | 0.8 | 0 | 12.4683 | 78 | 0 | 972.5295 | 12.4683 | 972.5295
610562 | Project A | Area4 | Sub Area 43 | Section 413 | C-10369 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610562 | Project A | Area4 | Sub Area 43 | Section 413 | C-10369 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6030 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610563 | Project A | Area4 | Sub Area 43 | Section 413 | C-10370 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 149 | 1 | Tray | 0.1946 | 28.9958 | IWP-6017 | 0.8 | 0 | 23.1966 | 78 | 0 | 1809.3371 | 23.1966 | 1809.3371
610563 | Project A | Area4 | Sub Area 43 | Section 413 | C-10370 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6030 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610563 | Project A | Area4 | Sub Area 43 | Section 413 | C-10370 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6030 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610564 | Project A | Area4 | Sub Area 43 | Section 413 | C-10371 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 149 | 1 | Tray | 0.1946 | 28.9958 | IWP-6017 | 0.8 | 0 | 23.1966 | 78 | 0 | 1809.3371 | 23.1966 | 1809.3371
610564 | Project A | Area4 | Sub Area 43 | Section 413 | C-10371 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6030 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610564 | Project A | Area4 | Sub Area 43 | Section 413 | C-10371 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6030 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610565 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10011 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | NA | Module | Install Tray CableCat6e | M | 23 | 1 | Tray | 0 | 0 | IWP-6020 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610566 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10012 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 23 | 1 | Tray | 0.03281 | 0.75463 | IWP-6020 | 0.75 | 0.56597 | 0 | 110 | 62.257 | 0 | 0.56597 | 62.257
610566 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10012 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6030 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610566 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10012 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6030 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610567 | Project A | Area4 | Sub Area 43 | Section 413 | C-10372 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 18 | 1 | Tray | 0.12988 | 2.3378 | IWP-6020 | 0.75 | 1.7534 | 0 | 110 | 192.8694 | 0 | 1.7534 | 192.8694
610567 | Project A | Area4 | Sub Area 43 | Section 413 | C-10372 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6030 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610567 | Project A | Area4 | Sub Area 43 | Section 413 | C-10372 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6031 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610568 | Project A | Area4 | Sub Area 43 | Section 413 | C-10373 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 18 | 1 | Tray | 0.12988 | 2.3378 | IWP-6020 | 0.75 | 1.7534 | 0 | 110 | 192.8694 | 0 | 1.7534 | 192.8694
610568 | Project A | Area4 | Sub Area 43 | Section 413 | C-10373 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610568 | Project A | Area4 | Sub Area 43 | Section 413 | C-10373 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6031 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610569 | Project A | Area4 | Sub Area 43 | Section 413 | C-10374 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 22 | 1 | Tray | 0.14331 | 3.1529 | IWP-6020 | 0.75 | 2.3647 | 0 | 110 | 260.1151 | 0 | 2.3647 | 260.1151
610569 | Project A | Area4 | Sub Area 43 | Section 413 | C-10374 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6031 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610569 | Project A | Area4 | Sub Area 43 | Section 413 | C-10374 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6031 | 0.75 | 1.584 | 0 | 110 | 174.24 | 0 | 1.584 | 174.24
610570 | Project A | Area4 | Sub Area 43 | Section 413 | C-10375 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable40c14awg Cu 600V TECK, Random Fill | M | 22 | 1 | Tray | 0.24811 | 5.4585 | IWP-6020 | 0.75 | 4.0939 | 0 | 110 | 450.3242 | 0 | 4.0939 | 450.3242
610570 | Project A | Area4 | Sub Area 43 | Section 413 | C-10375 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6031 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610570 | Project A | Area4 | Sub Area 43 | Section 413 | C-10375 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 80 | 1 |  | 0.132 | 10.56 | IWP-6031 | 0.75 | 7.92 | 0 | 110 | 871.2 | 0 | 7.92 | 871.2
610571 | Project A | Area4 | Sub Area 43 | Section 413 | P-10186 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install Tray Cable500mcm Cu 5kV Unshld TECK 90C | M | 100 | 1 | Tray | 0.53205 | 53.2053 | IWP-6018 | 0.8 | 0 | 42.5643 | 78 | 0 | 3320.0138 | 42.5643 | 3320.0138
610571 | Project A | Area4 | Sub Area 43 | Section 413 | P-10186 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6031 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610571 | Project A | Area4 | Sub Area 43 | Section 413 | P-10186 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6031 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610572 | Project A | Area4 | Sub Area 43 | Section 413 | P-10187 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 95 | 1 | Tray | 0.15809 | 15.0189 | IWP-6018 | 0.8 | 0 | 12.0151 | 78 | 0 | 937.1771 | 12.0151 | 937.1771
610572 | Project A | Area4 | Sub Area 43 | Section 413 | P-10187 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610572 | Project A | Area4 | Sub Area 43 | Section 413 | P-10187 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6031 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610573 | Project A | Area4 | Sub Area 43 | Section 413 | C-10376 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.75 | 0.396 | 0 | 110 | 43.56 | 0 | 0.396 | 43.56
610573 | Project A | Area4 | Sub Area 43 | Section 413 | C-10376 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 5 | 1 | Tray | 0.12316 | 0.6158 | IWP-6020 | 0.75 | 0.46185 | 0 | 110 | 50.8037 | 0 | 0.46185 | 50.8037
610573 | Project A | Area4 | Sub Area 43 | Section 413 | C-10376 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610574 | Project A | Area4 | Sub Area 43 | Section 413 | C-10377 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 132 | 1 | Tray | 0.12988 | 17.1439 | IWP-6018 | 0.8 | 0 | 13.7152 | 78 | 0 | 1069.7824 | 13.7152 | 1069.7824
610574 | Project A | Area4 | Sub Area 43 | Section 413 | C-10377 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610574 | Project A | Area4 | Sub Area 43 | Section 413 | C-10377 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6031 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610575 | Project A | Area4 | Sub Area 43 | Section 413 | C-10378 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 161 | 1 | Tray | 0.1946 | 31.331 | IWP-6018 | 0.8 | 0 | 25.0648 | 78 | 0 | 1955.0556 | 25.0648 | 1955.0556
610575 | Project A | Area4 | Sub Area 43 | Section 413 | C-10378 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6031 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610575 | Project A | Area4 | Sub Area 43 | Section 413 | C-10378 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6031 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610576 | Project A | Area4 | Sub Area 43 | Section 413 | C-10379 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable8triad 16awg 300V ACIC, Random Fill | M | 161 | 1 | Tray | 0.1946 | 31.331 | IWP-6018 | 0.8 | 0 | 25.0648 | 78 | 0 | 1955.0556 | 25.0648 | 1955.0556
610576 | Project A | Area4 | Sub Area 43 | Section 413 | C-10379 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6031 | 0.8 | 0 | 1.56 | 78 | 0 | 121.68 | 1.56 | 121.68
610576 | Project A | Area4 | Sub Area 43 | Section 413 | C-10379 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 32 | 1 |  | 0.132 | 4.224 | IWP-6031 | 0.8 | 0 | 3.3792 | 78 | 0 | 263.5776 | 3.3792 | 263.5776
610577 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10013 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | NA | Module | Install Tray CableCat6e | M | 23 | 1 | Tray | 0 | 0 | IWP-6020 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610578 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10014 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 23 | 1 | Tray | 0.03281 | 0.75463 | IWP-6020 | 0.75 | 0.56597 | 0 | 110 | 62.257 | 0 | 0.56597 | 62.257
610578 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10014 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6031 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610578 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10014 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6031 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610579 | Project A | Area4 | Sub Area 43 | Section 413 | C-10380 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12988 | 1.9482 | IWP-6020 | 0.75 | 1.4611 | 0 | 110 | 160.7245 | 0 | 1.4611 | 160.7245
610579 | Project A | Area4 | Sub Area 43 | Section 413 | C-10380 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610579 | Project A | Area4 | Sub Area 43 | Section 413 | C-10380 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6031 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610580 | Project A | Area4 | Sub Area 43 | Section 413 | C-10381 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable14awg CU 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12988 | 1.9482 | IWP-6020 | 0.75 | 1.4611 | 0 | 110 | 160.7245 | 0 | 1.4611 | 160.7245
610580 | Project A | Area4 | Sub Area 43 | Section 413 | C-10381 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.75 | 0.9945 | 0 | 110 | 109.395 | 0 | 0.9945 | 109.395
610580 | Project A | Area4 | Sub Area 43 | Section 413 | C-10381 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6031 | 0.75 | 0.792 | 0 | 110 | 87.12 | 0 | 0.792 | 87.12
610581 | Project A | Area4 | Sub Area 43 | Section 413 | C-10382 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Module | Install Tray Cable4pr16awg Shld 300V ACIC, Random Fill | M | 20 | 1 | Tray | 0.14331 | 2.8663 | IWP-6020 | 0.75 | 2.1497 | 0 | 110 | 236.4683 | 0 | 2.1497 | 236.4683
610581 | Project A | Area4 | Sub Area 43 | Section 413 | C-10382 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Module | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.975 | 1.95 | IWP-6031 | 0.75 | 1.4625 | 0 | 110 | 160.875 | 0 | 1.4625 | 160.875
610581 | Project A | Area4 | Sub Area 43 | Section 413 | C-10382 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Module | 300V Terminations | EA | 16 | 1 |  | 0.132 | 2.112 | IWP-6031 | 0.75 | 1.584 | 0 | 110 | 174.24 | 0 | 1.584 | 174.24
610582 | Project A | Area4 | Sub Area 43 | Section 413 | C-10383 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Module | Install Tray Cable40c14awg Cu 600V TECK, Random Fill | M | 20 | 1 | Tray | 0.24811 | 4.9623 | IWP-6020 | 0.75 | 3.7217 | 0 | 110 | 409.3856 | 0 | 3.7217 | 409.3856
610582 | Project A | Area4 | Sub Area 43 | Section 413 | C-10383 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Module | Install 1KV/600V Connectors | EA | 2 | 1 |  | 2.067 | 4.134 | IWP-6031 | 0.75 | 3.1005 | 0 | 110 | 341.055 | 0 | 3.1005 | 341.055
610582 | Project A | Area4 | Sub Area 43 | Section 413 | C-10383 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Module | 600V Terminations | EA | 80 | 1 |  | 0.132 | 10.56 | IWP-6031 | 0.75 | 7.92 | 0 | 110 | 871.2 | 0 | 7.92 | 871.2
610583 | Project A | Area4 | Sub Area 43 | Section 413 | P-10190 | 161 | 2 | 2 - Wire & Cable | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16122202002 | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Cable | 5kV | Field | Install Tray Cable500mcm Cu 5kV Unshld TECK 90C | M | 132 | 1 | Tray | 0.53205 | 70.2311 | IWP-6018 | 0.8 | 0 | 56.1848 | 78 | 0 | 4382.4183 | 56.1848 | 4382.4183
610583 | Project A | Area4 | Sub Area 43 | Section 413 | P-10190 | 161 | 3 | 3 - Connectors | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16132202002 | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Connector | 5kV | Field | Install 5kV Connectors | EA | 2 | 1 |  | 4.641 | 9.282 | IWP-6031 | 0.8 | 0 | 7.4256 | 78 | 0 | 579.1968 | 7.4256 | 579.1968
610583 | Project A | Area4 | Sub Area 43 | Section 413 | P-10190 | 161 | 4 | 4 - Terminations | 220 | 220 - MV Cable (2KV to 10KV) | 2002 | 2002 - 250 mcm to 500 mcm | 16142202002 | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Terminations | 5kV | Field | 5kV Terminations | EA | 6 | 1 |  | 6.5 | 39 | IWP-6031 | 0.8 | 0 | 31.2 | 78 | 0 | 2433.6 | 31.2 | 2433.6
610584 | Project A | Area4 | Sub Area 43 | Section 413 | P-10191 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16122302004 | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Cable | 600V | Field | Install Tray Cable10awg Cu 600V TECK, Random Fill | M | 126 | 1 | Tray | 0.15809 | 19.9198 | IWP-6018 | 0.8 | 0 | 15.9358 | 78 | 0 | 1242.9928 | 15.9358 | 1242.9928
610584 | Project A | Area4 | Sub Area 43 | Section 413 | P-10191 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16132302004 | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610584 | Project A | Area4 | Sub Area 43 | Section 413 | P-10191 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2004 | 2004 - AWG 12 to AWG 3 | 16142302004 | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Terminations | 600V | Field | 600V Terminations | EA | 6 | 1 |  | 0.176 | 1.056 | IWP-6031 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610585 | Project A | Area4 | Sub Area 43 | Section 413 | C-10384 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 24 | 1 | Tray | 0.10614 | 2.5474 | IWP-6018 | 0.8 | 0 | 2.0379 | 78 | 0 | 158.9583 | 2.0379 | 158.9583
610585 | Project A | Area4 | Sub Area 43 | Section 413 | C-10384 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610585 | Project A | Area4 | Sub Area 43 | Section 413 | C-10384 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6031 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610586 | Project A | Area4 | Sub Area 43 | Section 413 | C-10385 | 161 | 2 | 2 - Wire & Cable | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16122402005 | 16122402005 - Control/Instrument Cable - AWG14 and smaller | Cable | 300V | Field | Install Tray Cable2pr16awg Shld 300V ACIC, Random Fill | M | 24 | 1 | Tray | 0.10614 | 2.5474 | IWP-6018 | 0.8 | 0 | 2.0379 | 78 | 0 | 158.9583 | 2.0379 | 158.9583
610586 | Project A | Area4 | Sub Area 43 | Section 413 | C-10385 | 161 | 3 | 3 - Connectors | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16132402005 | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Connector | 300V | Field | Install 300V/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610586 | Project A | Area4 | Sub Area 43 | Section 413 | C-10385 | 161 | 4 | 4 - Terminations | 240 | 240 - Control/Instrument Cable | 2005 | 2005 - AWG14 and smaller | 16142402005 | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Terminations | 300V | Field | 300V Terminations | EA | 8 | 1 |  | 0.132 | 1.056 | IWP-6031 | 0.8 | 0 | 0.8448 | 78 | 0 | 65.8944 | 0.8448 | 65.8944
610587 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10015 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6020 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610587 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10015 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6031 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610587 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10015 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6031 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610588 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10016 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6020 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610588 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10016 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6031 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610588 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10016 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6031 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610589 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10017 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6020 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610589 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10017 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6031 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610589 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10017 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6031 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610590 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10018 | 161 | 2 | 2 - Wire & Cable | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16122709999 | 16122709999 - Fiberoptic Cable | Cable | Ethernet | Module | Install Tray CableCat6e Ethernet Cable, Armoured, Random Fill | M | 5 | 1 | Tray | 0.03281 | 0.16405 | IWP-6020 | 0.75 | 0.12304 | 0 | 110 | 13.5341 | 0 | 0.12304 | 13.5341
610590 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10018 | 161 | 3 | 3 - Connectors | 280 | 280 - Ethernet Cable | 9999 | 9999 - Not Applicable | 16132809999 | 16132809999 - Connectors - Ethernet Cable | Connector | Ethernet | Module | Install Ethernet Connectors | EA | 2 | 1 |  | 0 | 0 | IWP-6031 | 0.75 | 0 | 0 | 110 | 0 | 0 | 0 | 0
610590 | Project A | Area4 | Sub Area 43 | Section 413 | CAT-10018 | 161 | 4 | 4 - Terminations | 270 | 270 - Fiberoptic Cable | 9999 | 9999 - Not Applicable | 16142709999 | 16142709999 - Terminations - Fiberoptic Cable | Terminations | Ethernet | Module | Ethernet Terminations | EA | 10 | 1 |  | 0.13 | 1.3 | IWP-6031 | 0.75 | 0.975 | 0 | 110 | 107.25 | 0 | 0.975 | 107.25
610591 | Project A | Area4 | Sub Area 43 | Section 413 | C-10386 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610591 | Project A | Area4 | Sub Area 43 | Section 413 | C-10386 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.12316 | 9.8528 | IWP-6018 | 0.8 | 0 | 7.8823 | 78 | 0 | 614.8172 | 7.8823 | 614.8172
610591 | Project A | Area4 | Sub Area 43 | Section 413 | C-10386 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610592 | Project A | Area4 | Sub Area 43 | Section 413 | C-10387 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.12316 | 9.8528 | IWP-6018 | 0.8 | 0 | 7.8823 | 78 | 0 | 614.8172 | 7.8823 | 614.8172
610592 | Project A | Area4 | Sub Area 43 | Section 413 | C-10387 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610592 | Project A | Area4 | Sub Area 43 | Section 413 | C-10387 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610593 | Project A | Area4 | Sub Area 43 | Section 413 | C-10388 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610593 | Project A | Area4 | Sub Area 43 | Section 413 | C-10388 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.12316 | 9.8528 | IWP-6018 | 0.8 | 0 | 7.8823 | 78 | 0 | 614.8172 | 7.8823 | 614.8172
610593 | Project A | Area4 | Sub Area 43 | Section 413 | C-10388 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610594 | Project A | Area4 | Sub Area 43 | Section 413 | C-10389 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610594 | Project A | Area4 | Sub Area 43 | Section 413 | C-10389 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.12316 | 9.8528 | IWP-6018 | 0.8 | 0 | 7.8823 | 78 | 0 | 614.8172 | 7.8823 | 614.8172
610594 | Project A | Area4 | Sub Area 43 | Section 413 | C-10389 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610595 | Project A | Area4 | Sub Area 43 | Section 413 | C-10390 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610595 | Project A | Area4 | Sub Area 43 | Section 413 | C-10390 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12316 | 1.8474 | IWP-6018 | 0.8 | 0 | 1.4779 | 78 | 0 | 115.2782 | 1.4779 | 115.2782
610595 | Project A | Area4 | Sub Area 43 | Section 413 | C-10390 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610596 | Project A | Area4 | Sub Area 43 | Section 413 | C-10391 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610596 | Project A | Area4 | Sub Area 43 | Section 413 | C-10391 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12316 | 1.8474 | IWP-6018 | 0.8 | 0 | 1.4779 | 78 | 0 | 115.2782 | 1.4779 | 115.2782
610596 | Project A | Area4 | Sub Area 43 | Section 413 | C-10391 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610597 | Project A | Area4 | Sub Area 43 | Section 413 | C-10392 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610597 | Project A | Area4 | Sub Area 43 | Section 413 | C-10392 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12316 | 1.8474 | IWP-6018 | 0.8 | 0 | 1.4779 | 78 | 0 | 115.2782 | 1.4779 | 115.2782
610597 | Project A | Area4 | Sub Area 43 | Section 413 | C-10392 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610598 | Project A | Area4 | Sub Area 43 | Section 413 | C-10393 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610598 | Project A | Area4 | Sub Area 43 | Section 413 | C-10393 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 75 | 1 | Tray | 0.12316 | 9.237 | IWP-6018 | 0.8 | 0 | 7.3896 | 78 | 0 | 576.3911 | 7.3896 | 576.3911
610598 | Project A | Area4 | Sub Area 43 | Section 413 | C-10393 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610599 | Project A | Area4 | Sub Area 43 | Section 413 | C-10394 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610599 | Project A | Area4 | Sub Area 43 | Section 413 | C-10394 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 75 | 1 | Tray | 0.12316 | 9.237 | IWP-6018 | 0.8 | 0 | 7.3896 | 78 | 0 | 576.3911 | 7.3896 | 576.3911
610599 | Project A | Area4 | Sub Area 43 | Section 413 | C-10394 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610600 | Project A | Area4 | Sub Area 43 | Section 413 | C-10395 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610600 | Project A | Area4 | Sub Area 43 | Section 413 | C-10395 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 75 | 1 | Tray | 0.12316 | 9.237 | IWP-6018 | 0.8 | 0 | 7.3896 | 78 | 0 | 576.3911 | 7.3896 | 576.3911
610600 | Project A | Area4 | Sub Area 43 | Section 413 | C-10395 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610601 | Project A | Area4 | Sub Area 43 | Section 413 | C-10396 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610601 | Project A | Area4 | Sub Area 43 | Section 413 | C-10396 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12316 | 3.079 | IWP-6018 | 0.8 | 0 | 2.4632 | 78 | 0 | 192.1304 | 2.4632 | 192.1304
610601 | Project A | Area4 | Sub Area 43 | Section 413 | C-10396 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610602 | Project A | Area4 | Sub Area 43 | Section 413 | C-10397 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610602 | Project A | Area4 | Sub Area 43 | Section 413 | C-10397 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12316 | 3.079 | IWP-6018 | 0.8 | 0 | 2.4632 | 78 | 0 | 192.1304 | 2.4632 | 192.1304
610602 | Project A | Area4 | Sub Area 43 | Section 413 | C-10397 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610603 | Project A | Area4 | Sub Area 43 | Section 413 | C-10398 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 25 | 1 | Tray | 0.12316 | 3.079 | IWP-6018 | 0.8 | 0 | 2.4632 | 78 | 0 | 192.1304 | 2.4632 | 192.1304
610603 | Project A | Area4 | Sub Area 43 | Section 413 | C-10398 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610603 | Project A | Area4 | Sub Area 43 | Section 413 | C-10398 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610604 | Project A | Area4 | Sub Area 43 | Section 413 | C-10399 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 15 | 1 | Tray | 0.12316 | 1.8474 | IWP-6018 | 0.8 | 0 | 1.4779 | 78 | 0 | 115.2782 | 1.4779 | 115.2782
610604 | Project A | Area4 | Sub Area 43 | Section 413 | C-10399 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610604 | Project A | Area4 | Sub Area 43 | Section 413 | C-10399 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610605 | Project A | Area4 | Sub Area 43 | Section 413 | C-10400 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 35 | 1 | Tray | 0.12316 | 4.3106 | IWP-6018 | 0.8 | 0 | 3.4485 | 78 | 0 | 268.9825 | 3.4485 | 268.9825
610605 | Project A | Area4 | Sub Area 43 | Section 413 | C-10400 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610605 | Project A | Area4 | Sub Area 43 | Section 413 | C-10400 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610606 | Project A | Area4 | Sub Area 43 | Section 413 | C-10401 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.12316 | 9.8528 | IWP-6018 | 0.8 | 0 | 7.8823 | 78 | 0 | 614.8172 | 7.8823 | 614.8172
610606 | Project A | Area4 | Sub Area 43 | Section 413 | C-10401 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610606 | Project A | Area4 | Sub Area 43 | Section 413 | C-10401 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610607 | Project A | Area4 | Sub Area 43 | Section 413 | C-10402 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 120 | 1 | Tray | 0.12316 | 14.7793 | IWP-6018 | 0.8 | 0 | 11.8234 | 78 | 0 | 922.2258 | 11.8234 | 922.2258
610607 | Project A | Area4 | Sub Area 43 | Section 413 | C-10402 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610607 | Project A | Area4 | Sub Area 43 | Section 413 | C-10402 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610608 | Project A | Area4 | Sub Area 43 | Section 413 | C-10403 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 95 | 1 | Tray | 0.12316 | 11.7002 | IWP-6018 | 0.8 | 0 | 9.3602 | 78 | 0 | 730.0954 | 9.3602 | 730.0954
610608 | Project A | Area4 | Sub Area 43 | Section 413 | C-10403 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610608 | Project A | Area4 | Sub Area 43 | Section 413 | C-10403 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610609 | Project A | Area4 | Sub Area 43 | Section 413 | C-10404 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 80 | 1 | Tray | 0.12316 | 9.8528 | IWP-6018 | 0.8 | 0 | 7.8823 | 78 | 0 | 614.8172 | 7.8823 | 614.8172
610609 | Project A | Area4 | Sub Area 43 | Section 413 | C-10404 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610609 | Project A | Area4 | Sub Area 43 | Section 413 | C-10404 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610610 | Project A | Area4 | Sub Area 43 | Section 413 | C-10405 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 70 | 1 | Tray | 0.12316 | 8.6212 | IWP-6018 | 0.8 | 0 | 6.897 | 78 | 0 | 537.9651 | 6.897 | 537.9651
610610 | Project A | Area4 | Sub Area 43 | Section 413 | C-10405 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
610610 | Project A | Area4 | Sub Area 43 | Section 413 | C-10405 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610611 | Project A | Area4 | Sub Area 43 | Section 413 | C-10406 | 161 | 4 | 4 - Terminations | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16142302005 | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Terminations | 600V | Field | 600V Terminations | EA | 4 | 1 |  | 0.132 | 0.528 | IWP-6031 | 0.8 | 0 | 0.4224 | 78 | 0 | 32.9472 | 0.4224 | 32.9472
610611 | Project A | Area4 | Sub Area 43 | Section 413 | C-10406 | 161 | 2 | 2 - Wire & Cable | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16122302005 | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | Cable | 600V | Field | Install Tray Cable14awg Cu 600V TECK, Random Fill | M | 66 | 1 | Tray | 0.12316 | 8.1286 | IWP-6018 | 0.8 | 0 | 6.5029 | 78 | 0 | 507.2242 | 6.5029 | 507.2242
610611 | Project A | Area4 | Sub Area 43 | Section 413 | C-10406 | 161 | 3 | 3 - Connectors | 230 | 230 - LV Cable (1KV/600V) | 2005 | 2005 - AWG14 and smaller | 16132302005 | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Connector | 600V | Field | Install 1KV/600V Connectors | EA | 2 | 1 |  | 0.663 | 1.326 | IWP-6031 | 0.8 | 0 | 1.0608 | 78 | 0 | 82.7424 | 1.0608 | 82.7424
620001 | Project A | Area1 | Sub Area 11 | Section 111 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1005 | 1005 - 12 inch | 16111101005 | 16111101005 - Cable Tray - 12 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 40 | 0 |  | 0.69789 | 27.9155 | IWP-6002 | 0.8 | 0 | 22.3324 | 78 | 0 | 1741.9294 | 22.3324 | 1741.9294
620002 | Project A | Area1 | Sub Area 11 | Section 111 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 20 | 0 |  | 0.70804 | 14.1608 | IWP-6002 | 0.8 | 0 | 11.3286 | 78 | 0 | 883.6337 | 11.3286 | 883.6337
620003 | Project A | Area1 | Sub Area 11 | Section 111 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1005 | 1005 - 12 inch | 16111201005 | 16111201005 - Cable Tray Fittings - 12 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 2 | 0 |  | 4.2042 | 8.4084 | IWP-6002 | 0.8 | 0 | 6.7267 | 78 | 0 | 524.6842 | 6.7267 | 524.6842
620004 | Project A | Area1 | Sub Area 11 | Section 111 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1005 | 1005 - 12 inch | 16111201005 | 16111201005 - Cable Tray Fittings - 12 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 10 | 0 |  | 3.575 | 35.75 | IWP-6002 | 0.8 | 0 | 28.6 | 78 | 0 | 2230.8 | 28.6 | 2230.8
620005 | Project A | Area1 | Sub Area 11 | Section 111 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 4 | 0 |  | 4.5864 | 18.3456 | IWP-6002 | 0.8 | 0 | 14.6765 | 78 | 0 | 1144.7654 | 14.6765 | 1144.7654
620006 | Project A | Area1 | Sub Area 11 | Section 111 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 6 | 0 |  | 3.9 | 23.4 | IWP-6002 | 0.8 | 0 | 18.72 | 78 | 0 | 1460.16 | 18.72 | 1460.16
620007 | Project A | Area1 | Sub Area 12 | Section 112 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 30 | 0 |  | 0.69789 | 20.9367 | IWP-6002 | 0.8 | 0 | 16.7493 | 78 | 0 | 1306.4471 | 16.7493 | 1306.4471
620008 | Project A | Area1 | Sub Area 12 | Section 112 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 10 | 0 |  | 3.575 | 35.75 | IWP-6002 | 0.8 | 0 | 28.6 | 78 | 0 | 2230.8 | 28.6 | 2230.8
620009 | Project A | Area1 | Sub Area 12 | Section 112 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 45Elbow | Field | Install 45Elbow | EA | 10 | 0 |  | 2.34 | 23.4 | IWP-6002 | 0.8 | 0 | 18.72 | 78 | 0 | 1460.16 | 18.72 | 1460.16
620010 | Project A | Area1 | Sub Area 12 | Section 112 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Module | Install Aluminum Ladder Tray | M | 15 | 0 |  | 0.66342 | 9.9514 | IWP-6002 | 0.75 | 7.4635 | 0 | 110 | 820.9882 | 0 | 7.4635 | 820.9882
620011 | Project A | Area2 | Sub Area 21 | Section 211 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1003 | 1003 - 24 inch | 16111101003 | 16111101003 - Cable Tray - 24 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 40 | 0 |  | 0.69789 | 27.9155 | IWP-6003 | 0.8 | 0 | 22.3324 | 78 | 0 | 1741.9294 | 22.3324 | 1741.9294
620012 | Project A | Area2 | Sub Area 21 | Section 211 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 24 | 0 |  | 0.7524 | 18.0576 | IWP-6003 | 0.8 | 0 | 14.4461 | 78 | 0 | 1126.7926 | 14.4461 | 1126.7926
620013 | Project A | Area2 | Sub Area 21 | Section 211 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1003 | 1003 - 24 inch | 16111201003 | 16111201003 - Cable Tray Fittings - 24 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 2 | 0 |  | 6.8276 | 13.6552 | IWP-6003 | 0.8 | 0 | 10.9242 | 78 | 0 | 852.0845 | 10.9242 | 852.0845
620014 | Project A | Area2 | Sub Area 21 | Section 211 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1003 | 1003 - 24 inch | 16111201003 | 16111201003 - Cable Tray Fittings - 24 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 4 | 0 |  | 5.5341 | 22.1364 | IWP-6003 | 0.8 | 0 | 17.7091 | 78 | 0 | 1381.3114 | 17.7091 | 1381.3114
620015 | Project A | Area2 | Sub Area 21 | Section 211 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 10 | 0 |  | 4.2042 | 42.042 | IWP-6003 | 0.8 | 0 | 33.6336 | 78 | 0 | 2623.4208 | 33.6336 | 2623.4208
620016 | Project A | Area2 | Sub Area 21 | Section 211 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 26 | 0 |  | 3.575 | 92.95 | IWP-6003 | 0.8 | 0 | 74.36 | 78 | 0 | 5800.08 | 74.36 | 5800.08
620017 | Project A | Area2 | Sub Area 21 | Section 211 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1003 | 1003 - 24 inch | 16111101003 | 16111101003 - Cable Tray - 24 inch | Tray | Al_Tray | Module | Install Aluminum Ladder Tray | M | 12 | 0 |  | 0.66342 | 7.9611 | IWP-6003 | 0.75 | 5.9708 | 0 | 110 | 656.7906 | 0 | 5.9708 | 656.7906
620018 | Project A | Area2 | Sub Area 22 | Section 212 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 50 | 0 |  | 0.69789 | 34.8944 | IWP-6004 | 0.8 | 0 | 27.9155 | 78 | 0 | 2177.4118 | 27.9155 | 2177.4118
620019 | Project A | Area2 | Sub Area 22 | Section 212 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 10 | 0 |  | 3.575 | 35.75 | IWP-6004 | 0.8 | 0 | 28.6 | 78 | 0 | 2230.8 | 28.6 | 2230.8
620020 | Project A | Area2 | Sub Area 22 | Section 212 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 45Elbow | Field | Install 45Elbow | EA | 10 | 0 |  | 2.34 | 23.4 | IWP-6004 | 0.8 | 0 | 18.72 | 78 | 0 | 1460.16 | 18.72 | 1460.16
620021 | Project A | Area2 | Sub Area 22 | Section 212 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Module | Install Aluminum Ladder Tray | M | 6 | 0 |  | 0.66342 | 3.9805 | IWP-6004 | 0.75 | 2.9854 | 0 | 110 | 328.3953 | 0 | 2.9854 | 328.3953
620022 | Project A | Area3 | Sub Area 31 | Section 311 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 15 | 0 |  | 0.69789 | 10.4683 | IWP-6004 | 0.8 | 0 | 8.3747 | 78 | 0 | 653.2235 | 8.3747 | 653.2235
620023 | Project A | Area3 | Sub Area 31 | Section 311 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 10 | 0 |  | 3.575 | 35.75 | IWP-6004 | 0.8 | 0 | 28.6 | 78 | 0 | 2230.8 | 28.6 | 2230.8
620024 | Project A | Area3 | Sub Area 31 | Section 311 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 45Elbow | Field | Install 45Elbow | EA | 10 | 0 |  | 2.34 | 23.4 | IWP-6004 | 0.8 | 0 | 18.72 | 78 | 0 | 1460.16 | 18.72 | 1460.16
620025 | Project A | Area3 | Sub Area 31 | Section 311 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Module | Install Aluminum Ladder Tray | M | 25 | 0 |  | 0.66342 | 16.5856 | IWP-6004 | 0.75 | 12.4392 | 0 | 110 | 1368.3137 | 0 | 12.4392 | 1368.3137
620026 | Project A | Area3 | Sub Area 31 | Section 311 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Module | Install 90Elbow | M | 4 | 0 |  | 2.9601 | 11.8404 | IWP-6004 | 0.75 | 8.8803 | 0 | 110 | 976.833 | 0 | 8.8803 | 976.833
620027 | Project A | Area3 | Sub Area 32 | Section 312 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1002 | 1002 - 30 inch | 16111101002 | 16111101002 - Cable Tray - 30 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 20 | 0 |  | 0.72207 | 14.4415 | IWP-6005 | 0.8 | 0 | 11.5532 | 78 | 0 | 901.1467 | 11.5532 | 901.1467
620028 | Project A | Area3 | Sub Area 32 | Section 312 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 40 | 0 |  | 0.69789 | 27.9155 | IWP-6005 | 0.8 | 0 | 22.3324 | 78 | 0 | 1741.9294 | 22.3324 | 1741.9294
620029 | Project A | Area3 | Sub Area 32 | Section 312 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1002 | 1002 - 30 inch | 16111201002 | 16111201002 - Cable Tray Fittings - 30 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 2 | 0 |  | 5.85 | 11.7 | IWP-6005 | 0.8 | 0 | 9.36 | 78 | 0 | 730.08 | 9.36 | 730.08
620030 | Project A | Area3 | Sub Area 32 | Section 312 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1002 | 1002 - 30 inch | 16111201002 | 16111201002 - Cable Tray Fittings - 30 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 2 | 0 |  | 4.8906 | 9.7812 | IWP-6005 | 0.8 | 0 | 7.825 | 78 | 0 | 610.3469 | 7.825 | 610.3469
620031 | Project A | Area3 | Sub Area 32 | Section 312 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 6 | 0 |  | 4.2042 | 25.2252 | IWP-6005 | 0.8 | 0 | 20.1802 | 78 | 0 | 1574.0525 | 20.1802 | 1574.0525
620032 | Project A | Area3 | Sub Area 32 | Section 312 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 30 | 0 |  | 3.575 | 107.25 | IWP-6005 | 0.8 | 0 | 85.8 | 78 | 0 | 6692.4 | 85.8 | 6692.4
620033 | Project A | Area4 | Sub Area 41 | Section 411 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1005 | 1005 - 12 inch | 16111101005 | 16111101005 - Cable Tray - 12 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 50 | 0 |  | 0.69789 | 34.8944 | IWP-6005 | 0.8 | 0 | 27.9155 | 78 | 0 | 2177.4118 | 27.9155 | 2177.4118
620034 | Project A | Area4 | Sub Area 41 | Section 411 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1005 | 1005 - 12 inch | 16111101005 | 16111101005 - Cable Tray - 12 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 20 | 0 |  | 0.72207 | 14.4415 | IWP-6005 | 0.8 | 0 | 11.5532 | 78 | 0 | 901.1467 | 11.5532 | 901.1467
620035 | Project A | Area4 | Sub Area 41 | Section 411 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1005 | 1005 - 12 inch | 16111201005 | 16111201005 - Cable Tray Fittings - 12 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 6 | 0 |  | 4.2042 | 25.2252 | IWP-6005 | 0.8 | 0 | 20.1802 | 78 | 0 | 1574.0525 | 20.1802 | 1574.0525
620036 | Project A | Area4 | Sub Area 41 | Section 411 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1005 | 1005 - 12 inch | 16111201005 | 16111201005 - Cable Tray Fittings - 12 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 10 | 0 |  | 3.575 | 35.75 | IWP-6005 | 0.8 | 0 | 28.6 | 78 | 0 | 2230.8 | 28.6 | 2230.8
620037 | Project A | Area4 | Sub Area 41 | Section 411 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1005 | 1005 - 12 inch | 16111201005 | 16111201005 - Cable Tray Fittings - 12 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 2 | 0 |  | 5.85 | 11.7 | IWP-6005 | 0.8 | 0 | 9.36 | 78 | 0 | 730.08 | 9.36 | 730.08
620038 | Project A | Area4 | Sub Area 41 | Section 411 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1005 | 1005 - 12 inch | 16111201005 | 16111201005 - Cable Tray Fittings - 12 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 4 | 0 |  | 4.8906 | 19.5624 | IWP-6005 | 0.8 | 0 | 15.6499 | 78 | 0 | 1220.6938 | 15.6499 | 1220.6938
620039 | Project A | Area4 | Sub Area 41 | Section 411 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1005 | 1005 - 12 inch | 16111101005 | 16111101005 - Cable Tray - 12 inch | Tray | Al_Tray | Module | Install Aluminum Ladder Tray | M | 50 | 0 |  | 0.66342 | 33.1712 | IWP-6005 | 0.75 | 24.8784 | 0 | 110 | 2736.6273 | 0 | 24.8784 | 2736.6273
620040 | Project A | Area4 | Sub Area 42 | Section 412 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 15 | 0 |  | 0.69789 | 10.4683 | IWP-6006 | 0.8 | 0 | 8.3747 | 78 | 0 | 653.2235 | 8.3747 | 653.2235
620041 | Project A | Area4 | Sub Area 42 | Section 412 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 10 | 0 |  | 3.575 | 35.75 | IWP-6006 | 0.8 | 0 | 28.6 | 78 | 0 | 2230.8 | 28.6 | 2230.8
620042 | Project A | Area4 | Sub Area 42 | Section 412 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 45Elbow | Field | Install 45Elbow | EA | 10 | 0 |  | 2.34 | 23.4 | IWP-6006 | 0.8 | 0 | 18.72 | 78 | 0 | 1460.16 | 18.72 | 1460.16
620043 | Project A | Area4 | Sub Area 42 | Section 412 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Module | Install Aluminum Ladder Tray | M | 15 | 0 |  | 0.66342 | 9.9514 | IWP-6006 | 0.75 | 7.4635 | 0 | 110 | 820.9882 | 0 | 7.4635 | 820.9882
620044 | Project A | Area4 | Sub Area 42 | Section 412 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Module | Install Aluminum Ladder Tray | M | 3 | 0 |  | 2.9601 | 8.8803 | IWP-6006 | 0.75 | 6.6602 | 0 | 110 | 732.6248 | 0 | 6.6602 | 732.6248
620045 | Project A | Area4 | Sub Area 43 | Section 413 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Field | Install Aluminum Ladder Tray | M | 25 | 0 |  | 0.69789 | 17.4472 | IWP-6007 | 0.8 | 0 | 13.9578 | 78 | 0 | 1088.7059 | 13.9578 | 1088.7059
620046 | Project A | Area4 | Sub Area 43 | Section 413 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow_Vertical | Field | Install 90Elbow_Vertical | EA | 10 | 0 |  | 4.2042 | 42.042 | IWP-6007 | 0.8 | 0 | 33.6336 | 78 | 0 | 2623.4208 | 33.6336 | 2623.4208
620047 | Project A | Area4 | Sub Area 43 | Section 413 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | 90Elbow | Field | Install 90Elbow | EA | 30 | 0 |  | 3.575 | 107.25 | IWP-6007 | 0.8 | 0 | 85.8 | 78 | 0 | 6692.4 | 85.8 | 6692.4
620048 | Project A | Area4 | Sub Area 43 | Section 413 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | Cross | Field | Install Cross | EA | 2 | 0 |  | 8.32 | 16.64 | IWP-6007 | 0.8 | 0 | 13.312 | 78 | 0 | 1038.336 | 13.312 | 1038.336
620049 | Project A | Area4 | Sub Area 43 | Section 413 |  | 161 | 1 | 1 - Cable Tray/Conduit | 120 | 120 - Cable Tray Fittings | 1006 | 1006 - 6 inch | 16111201006 | 16111201006 - Cable Tray Fittings - 6 inch | Tray | Tee | Field | Install Tee | EA | 1 | 0 |  | 6.1152 | 6.1152 | IWP-6007 | 0.8 | 0 | 4.8922 | 78 | 0 | 381.5885 | 4.8922 | 381.5885
620050 | Project A | Area4 | Sub Area 43 | Section 413 |  | 161 | 1 | 1 - Cable Tray/Conduit | 110 | 110 - Cable Tray | 1006 | 1006 - 6 inch | 16111101006 | 16111101006 - Cable Tray - 6 inch | Tray | Al_Tray | Module | Install Aluminum Ladder Tray | M | 15 | 0 |  | 0.66342 | 9.9514 | IWP-6007 | 0.75 | 7.4635 | 0 | 110 | 820.9882 | 0 | 7.4635 | 820.9882
630001 | Project A | Area1 | Sub Area 12 | Section 112 |  | 161 | 1 | 1 - Cable Tray/Conduit | 150 | 150 - Conduits | 1007 | 1007 - 4 inch and below | 16111501007 | 16111501007 - Conduits - 4 inch and below | Conduit AG | RS | Field | Install Rigid Steel Conduit AG Composite | M | 400 | 0 |  | 1.0516 | 420.6408 | IWP-6001 | 0.8 | 0 | 336.5126 | 78 | 0 | 26247.9859 | 336.5126 | 26247.9859
630002 | Project A | Area1 | Sub Area 12 | Section 112 |  | 161 | 1 | 1 - Cable Tray/Conduit | 150 | 150 - Conduits | 1007 | 1007 - 4 inch and below | 16111501007 | 16111501007 - Conduits - 4 inch and below | Conduit AG | RS | Field | Install Rigid Steel Conduit AG Composite | M | 500 | 0 |  | 0.48501 | 242.5069 | IWP-6001 | 0.8 | 0 | 194.0055 | 78 | 0 | 15132.4306 | 194.0055 | 15132.4306
9000001 | Project A | Area1 | Sub Area 11 | Section 111 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 3.8623 | 3.8623 | IWP-9999 | 0.75 | 2.8967 | 0 | 110 | 318.6359 | 0 | 2.8967 | 318.6359
9000001 | Project A | Area1 | Sub Area 11 | Section 111 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 12.3131 | 12.3131 | IWP-9999 | 0.8 | 0 | 9.8505 | 78 | 0 | 768.3393 | 9.8505 | 768.3393
9000001 | Project A | Area1 | Sub Area 12 | Section 112 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 6.5188 | 6.5188 | IWP-9999 | 0.75 | 4.8891 | 0 | 110 | 537.7979 | 0 | 4.8891 | 537.7979
9000001 | Project A | Area1 | Sub Area 12 | Section 112 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 46.7431 | 46.7431 | IWP-9999 | 0.8 | 0 | 37.3945 | 78 | 0 | 2916.7682 | 37.3945 | 2916.7682
9000001 | Project A | Area2 | Sub Area 21 | Section 211 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 10.0594 | 10.0594 | IWP-9999 | 0.75 | 7.5445 | 0 | 110 | 829.8964 | 0 | 7.5445 | 829.8964
9000001 | Project A | Area2 | Sub Area 21 | Section 211 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 75.8953 | 75.8953 | IWP-9999 | 0.8 | 0 | 60.7163 | 78 | 0 | 4735.868 | 60.7163 | 4735.868
9000001 | Project A | Area2 | Sub Area 22 | Section 212 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 0.19903 | 0.19903 | IWP-9999 | 0.75 | 0.14927 | 0 | 110 | 16.4198 | 0 | 0.14927 | 16.4198
9000001 | Project A | Area2 | Sub Area 22 | Section 212 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 4.7022 | 4.7022 | IWP-9999 | 0.8 | 0 | 3.7618 | 78 | 0 | 293.4186 | 3.7618 | 293.4186
9000001 | Project A | Area2 | Sub Area 22 | Section 221 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 18.7137 | 18.7137 | IWP-9999 | 0.75 | 14.0353 | 0 | 110 | 1543.8819 | 0 | 14.0353 | 1543.8819
9000001 | Project A | Area2 | Sub Area 22 | Section 221 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 63.8733 | 63.8733 | IWP-9999 | 0.8 | 0 | 51.0986 | 78 | 0 | 3985.6927 | 51.0986 | 3985.6927
9000001 | Project A | Area3 | Sub Area 31 | Section 311 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 2.0993 | 2.0993 | IWP-9999 | 0.75 | 1.5745 | 0 | 110 | 173.19 | 0 | 1.5745 | 173.19
9000001 | Project A | Area3 | Sub Area 31 | Section 311 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 24.3823 | 24.3823 | IWP-9999 | 0.8 | 0 | 19.5058 | 78 | 0 | 1521.453 | 19.5058 | 1521.453
9000001 | Project A | Area3 | Sub Area 32 | Section 312 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 30.368 | 30.368 | IWP-9999 | 0.8 | 0 | 24.2944 | 78 | 0 | 1894.9613 | 24.2944 | 1894.9613
9000001 | Project A | Area4 | Sub Area 41 | Section 411 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 4.4631 | 4.4631 | IWP-9999 | 0.75 | 3.3473 | 0 | 110 | 368.2065 | 0 | 3.3473 | 368.2065
9000001 | Project A | Area4 | Sub Area 41 | Section 411 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 79.1247 | 79.1247 | IWP-9999 | 0.8 | 0 | 63.2997 | 78 | 0 | 4937.38 | 63.2997 | 4937.38
9000001 | Project A | Area4 | Sub Area 42 | Section 412 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 8.9746 | 8.9746 | IWP-9999 | 0.75 | 6.731 | 0 | 110 | 740.4071 | 0 | 6.731 | 740.4071
9000001 | Project A | Area4 | Sub Area 42 | Section 412 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 36.6557 | 36.6557 | IWP-9999 | 0.8 | 0 | 29.3246 | 78 | 0 | 2287.3169 | 29.3246 | 2287.3169
9000001 | Project A | Area4 | Sub Area 43 | Section 413 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Module | Miscellaneous Items in Area | Lot | 1 | 0 |  | 8.3943 | 8.3943 | IWP-9999 | 0.75 | 6.2958 | 0 | 110 | 692.5329 | 0 | 6.2958 | 692.5329
9000001 | Project A | Area4 | Sub Area 43 | Section 413 | Allowance | 161 | 9 | 9 - Allowances | 910 | 910 - Allowance for Miscellaneous Items | 9109 | 9109 - Allowance | 16199109109 | 16199109109 - Allowance for Miscellaneous Items | Allowance | Allowance | Field | Miscellaneous Items in Area | Lot | 1 | 0 |  | 51.0571 | 51.0571 | IWP-9999 | 0.8 | 0 | 40.8457 | 78 | 0 | 3185.9655 | 40.8457 | 3185.9655
Electrical Bulks MTO Input Required - Wire & Cable
Example - Imaginary Project with made up quantities for Illustration Purposes
Electrical Bulks Labor Detail - Trace back to the source MTO Line Item by MTO_ID
Example - Imaginary Project with made up quantities for Illustration Purposes
Go to Tab Index
Note on Z9: Allocation of scope to various Installation Work Packages (IWPs) and scheduling of the IWPs are to be done by the project construction planning team giving due consideration to constructability and the estimated total location hours for the various IWPs. They can be refined during/after the first pass estimate review when the estimated location hours become available. Precise allocation of hours as in the actual control base estimate will make identification of overruns/underruns very expedient and enable timely corrective actions, as opposed to IWP hours allocated as standalone/disconnected estimates independent of the control base estimate.

## Output-Labor Summary Overview
Location | Item_Group | Size Group | Unit | Item Quantity | Field Hours | Field Cost | Module Hours | Module Cost | Total Cost
Field | 110 - Cable Tray | 16111101002 - Cable Tray - 30 inch | m | 20 | 12 | 901 | 0 | 0 | 901
Field | 110 - Cable Tray | 16111101003 - Cable Tray - 24 inch | m | 40 | 22 | 1742 | 0 | 0 | 1742
Field | 110 - Cable Tray | 16111101005 - Cable Tray - 12 inch | m | 110 | 62 | 4820 | 0 | 0 | 4820
Field | 110 - Cable Tray | 16111101006 - Cable Tray - 6 inch | m | 219 | 123 | 9631 | 0 | 0 | 9631
| 110 - Cable Tray Total |  | m | 389 | 219 | 17094 | 0 | 0 | 17094
Field | 120 - Cable Tray Fittings | 16111201002 - Cable Tray Fittings - 30 inch | Ea | 4 | 17 | 1340 | 0 | 0 | 1340
Field | 120 - Cable Tray Fittings | 16111201003 - Cable Tray Fittings - 24 inch | Ea | 6 | 29 | 2233 | 0 | 0 | 2233
Field | 120 - Cable Tray Fittings | 16111201005 - Cable Tray Fittings - 12 inch | Ea | 34 | 109 | 8511 | 0 | 0 | 8511
Field | 120 - Cable Tray Fittings | 16111201006 - Cable Tray Fittings - 6 inch | Ea | 205 | 574 | 44794 | 0 | 0 | 44794
| 120 - Cable Tray Fittings Total |  | Ea | 249 | 729 | 56878 | 0 | 0 | 56878
Field | 150 - Conduits | 16111501007 - Conduits - 4 inch and below | m | 900 | 531 | 41380 | 0 | 0 | 41380
| 150 - Conduits Total |  | m | 900 | 531 | 41380 | 0 | 0 | 41380
Field | 220 - MV Cable (2KV to 10KV) | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | m | 545 | 196 | 15293 | 0 | 0 | 15293
Field | 220 - MV Cable (2KV to 10KV) | 16122202003 - MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | m | 15 | 3 | 264 | 0 | 0 | 264
Field | 220 - MV Cable (2KV to 10KV) | 16122202004 - MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | m | 38 | 5 | 353 | 0 | 0 | 353
Field | 220 - MV Cable (2KV to 10KV) | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Ea | 18 | 67 | 5213 | 0 | 0 | 5213
Field | 220 - MV Cable (2KV to 10KV) | 16132202003 - Connectors - MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | Ea | 2 | 4 | 350 | 0 | 0 | 350
Field | 220 - MV Cable (2KV to 10KV) | 16132202004 - Connectors - MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | Ea | 2 | 3 | 258 | 0 | 0 | 258
Field | 220 - MV Cable (2KV to 10KV) | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Ea | 54 | 281 | 21902 | 0 | 0 | 21902
Field | 220 - MV Cable (2KV to 10KV) | 16142202003 - Terminations - MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | Ea | 6 | 17 | 1338 | 0 | 0 | 1338
Field | 220 - MV Cable (2KV to 10KV) | 16142202004 - Terminations - MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | Ea | 6 | 1 | 56 | 0 | 0 | 56
| 220 - MV Cable (2KV to 10KV) Total |  | m of Cable | 598 | 577 | 45027 | 0 | 0 | 45027
Field | 230 - LV Cable (1KV/600V) | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | m | 155 | 56 | 4354 | 0 | 0 | 4354
Field | 230 - LV Cable (1KV/600V) | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | m | 80 | 17 | 1310 | 0 | 0 | 1310
Field | 230 - LV Cable (1KV/600V) | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | m | 9774 | 1231 | 95981 | 0 | 0 | 95981
Field | 230 - LV Cable (1KV/600V) | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | m | 9335 | 1362 | 106209 | 0 | 0 | 106209
Field | 230 - LV Cable (1KV/600V) | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Ea | 10 | 25 | 1966 | 0 | 0 | 1966
Field | 230 - LV Cable (1KV/600V) | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Ea | 8 | 18 | 1402 | 0 | 0 | 1402
Field | 230 - LV Cable (1KV/600V) | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Ea | 194 | 126 | 9818 | 0 | 0 | 9818
Field | 230 - LV Cable (1KV/600V) | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Ea | 288 | 225 | 17548 | 0 | 0 | 17548
Field | 230 - LV Cable (1KV/600V) | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Ea | 30 | 18 | 1411 | 0 | 0 | 1411
Field | 230 - LV Cable (1KV/600V) | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Ea | 24 | 11 | 876 | 0 | 0 | 876
Field | 230 - LV Cable (1KV/600V) | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Ea | 592 | 88 | 6849 | 0 | 0 | 6849
Field | 230 - LV Cable (1KV/600V) | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Ea | 2936 | 310 | 24183 | 0 | 0 | 24183
| 230 - LV Cable (1KV/600V) Total |  | m of Cable | 19344 | 3487 | 271907 | 0 | 0 | 271907
Field | 240 - Control/Instrument Cable | 16122402005 - Control/Instrument Cable - AWG14 and smaller | m | 7945 | 913 | 71229 | 0 | 0 | 71229
Field | 240 - Control/Instrument Cable | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Ea | 236 | 155 | 12114 | 0 | 0 | 12114
Field | 240 - Control/Instrument Cable | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Ea | 1454 | 154 | 11976 | 0 | 0 | 11976
| 240 - Control/Instrument Cable Total |  | m of Cable | 7945 | 1222 | 95319 | 0 | 0 | 95319
Field | 270 - Fiberoptic Cable | 16122709999 - Fiberoptic Cable | m | 333 | 14 | 1117 | 0 | 0 | 1117
Field | 270 - Fiberoptic Cable | 16132709999 - Connectors - Fiberoptic Cable | Ea | 2 | 3 | 260 | 0 | 0 | 260
Field | 270 - Fiberoptic Cable | 16142709999 - Terminations - Fiberoptic Cable | Ea | 48 | 20 | 1558 | 0 | 0 | 1558
| 270 - Fiberoptic Cable Total |  | m of Cable | 333 | 37 | 2935 | 0 | 0 | 2935
Field | 910 - Allowance for Miscellaneous Items | 16199109109 - Allowance for Miscellaneous Items | 5% of Labor hours |  | 340 | 26527 | 0 | 0 | 26527
| 910 - Allowance for Miscellaneous Items Total |  | Lot |  | 340 | 26527 | 0 | 0 | 26527
Field Total |  |  |  |  | 7142 | 557067 | 0 | 0 | 557067
Module | 110 - Cable Tray | 16111101003 - Cable Tray - 24 inch | m | 12 | 0 | 0 | 6 | 657 | 657
Module | 110 - Cable Tray | 16111101005 - Cable Tray - 12 inch | m | 50 | 0 | 0 | 25 | 2737 | 2737
Module | 110 - Cable Tray | 16111101006 - Cable Tray - 6 inch | m | 76 | 0 | 0 | 38 | 4160 | 4160
| 110 - Cable Tray Total |  | m | 138 | 0 | 0 | 69 | 7554 | 7554
Module | 120 - Cable Tray Fittings | 16111201006 - Cable Tray Fittings - 6 inch | Ea | 7 | 0 | 0 | 16 | 1709 | 1709
| 120 - Cable Tray Fittings Total |  | Ea | 7 | 0 | 0 | 16 | 1709 | 1709
Module | 220 - MV Cable (2KV to 10KV) | 16122202002 - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | m | 66 | 0 | 0 | 26 | 2897 | 2897
Module | 220 - MV Cable (2KV to 10KV) | 16132202002 - Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Ea | 6 | 0 | 0 | 21 | 2297 | 2297
Module | 220 - MV Cable (2KV to 10KV) | 16142202002 - Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Ea | 18 | 0 | 0 | 88 | 9653 | 9653
| 220 - MV Cable (2KV to 10KV) Total |  | m of Cable | 90 | 0 | 0 | 135 | 14847 | 14847
Module | 230 - LV Cable (1KV/600V) | 16122302002 - LV Cable (1KV/600V) - 250 mcm to 500 mcm | m | 10 | 0 | 0 | 3 | 377 | 377
Module | 230 - LV Cable (1KV/600V) | 16122302003 - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | m | 137 | 0 | 0 | 27 | 3017 | 3017
Module | 230 - LV Cable (1KV/600V) | 16122302004 - LV Cable (1KV/600V) - AWG 12 to AWG 3 | m | 591 | 0 | 0 | 66 | 7276 | 7276
Module | 230 - LV Cable (1KV/600V) | 16122302005 - LV Cable (1KV/600V) - AWG14 and smaller | m | 757 | 0 | 0 | 89 | 9819 | 9819
Module | 230 - LV Cable (1KV/600V) | 16132302002 - Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Ea | 4 | 0 | 0 | 11 | 1210 | 1210
Module | 230 - LV Cable (1KV/600V) | 16132302003 - Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Ea | 26 | 0 | 0 | 33 | 3660 | 3660
Module | 230 - LV Cable (1KV/600V) | 16132302004 - Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Ea | 88 | 0 | 0 | 55 | 6017 | 6017
Module | 230 - LV Cable (1KV/600V) | 16132302005 - Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Ea | 134 | 0 | 0 | 99 | 10914 | 10914
Module | 230 - LV Cable (1KV/600V) | 16142302002 - Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Ea | 16 | 0 | 0 | 9 | 944 | 944
Module | 230 - LV Cable (1KV/600V) | 16142302003 - Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Ea | 58 | 0 | 0 | 18 | 1995 | 1995
Module | 230 - LV Cable (1KV/600V) | 16142302004 - Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Ea | 332 | 0 | 0 | 44 | 4809 | 4809
Module | 230 - LV Cable (1KV/600V) | 16142302005 - Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Ea | 1352 | 0 | 0 | 134 | 14723 | 14723
| 230 - LV Cable (1KV/600V) Total |  | m of Cable | 1495 | 0 | 0 | 588 | 64761 | 64761
Module | 240 - Control/Instrument Cable | 16122402005 - Control/Instrument Cable - AWG14 and smaller | m | 1229 | 0 | 0 | 54 | 5957 | 5957
Module | 240 - Control/Instrument Cable | 16132402005 - Connectors - Control/Instrument Cable - AWG14 and smaller | Ea | 168 | 0 | 0 | 105 | 11526 | 11526
Module | 240 - Control/Instrument Cable | 16142402005 - Terminations - Control/Instrument Cable - AWG14 and smaller | Ea | 578 | 0 | 0 | 57 | 6294 | 6294
| 240 - Control/Instrument Cable Total |  | m of Cable | 1975 | 0 | 0 | 216 | 23777 | 23777
Module | 270 - Fiberoptic Cable | 16122709999 - Fiberoptic Cable | m | 225 | 0 | 0 | 3 | 368 | 368
Module | 270 - Fiberoptic Cable | 16142709999 - Terminations - Fiberoptic Cable | m | 140 | 0 | 0 | 14 | 1502 | 1502
| 270 - Fiberoptic Cable Total |  | m of Cable | 225 | 0 | 0 | 17 | 1870 | 1870
Module | 280 - Ethernet Cable | 16132809999 - Connectors - Ethernet Cable | m | 28 | 0 | 0 | 0 | 0 | 0
| 280 - Ethernet Cable Total |  | m of Cable | 28 | 0 | 0 | 0 | 0 | 0
Module | 910 - Allowance for Miscellaneous Items | 16199109109 - Allowance for Miscellaneous Items | 5% of Labor hours |  | 0 | 0 | 47 | 5221 | 5221
| 910 - Allowance for Miscellaneous Items Total |  | Lot |  | 0 | 0 | 47 | 5221 | 5221
Module Total |  |  |  |  | 0 | 0 | 1088 | 119739 | 119739
Grand Total |  |  |  |  | 7142 | 557067 | 1088 | 119739 | 676806
Electrical Bulks Labor Summary - Field and Module Quantities, Craft Labor Hours and Cost by Item Group and Size
Example - Imaginary Project with made up quantities for Illustration Purposes See Interactive Power BI Report on the website for more estimate insights
Go to Tab Index

## Output-Quantities & Metrics
Field Quantities and Metrics
Field Cable Metric | FCM Value | Area | Field Hours | Category | Field Hours
Field Cable - M | 28220 | Area1 | 992 | Cable | 3796
Field Cable Hours incl. Termination - Hrs | 7142 | Area2 | 2427 | Tray | 948
Field Hours per M of Cable - Hrs/M | 0.25 | Area3 | 920 | Terminations | 899
|  | Area4 | 2803 | Connector | 627
|  | Total | 7142 | Conduit AG | 531
|  |  |  | Allowance | 340
|  |  |  | Total | 7141
Module Quantities and Metrics
Module Cable Metric | MCM Value | Area | Module Hours | Category | Module Hours
Module Cable - M | 3015 | Area1 | 256 | Cable | 270
Module Cable Hours incl. Termination - Hrs | 1089 | Area2 | 456 | Tray | 84
Module Hours per M of Cable - Hrs/M | 0.36 | Area3 | 33 | Terminations | 363
|  | Area4 | 344 | Connector | 324
|  | Total | 1089 | Allowance | 47
|  |  |  | Total | 1088
Total Quantities
Quantity Metric | QM Value
Total Cable - M | 31235
MV Cable (2KV to 10KV) - M | 664
LV Cable (1KV/600V) - M | 20839
Control/Instrument Cable - M | 9174
Fiber Optic Cable - M | 558
Electrical Bulks Field and Module Quantities, Craft Labor Hours and Metrics
Example - Imaginary Project with made up quantities for Illustration Purposes See Interactive Power BI Report on the website for more estimate insights
Go to Tab Index

## Labor Codes
COA | COA_Description | Units
16111101001 | Cable Tray - 36 inch | M
16111101002 | Cable Tray - 30 inch | M
16111101003 | Cable Tray - 24 inch | M
16111101004 | Cable Tray - 18 inch | M
16111101005 | Cable Tray - 12 inch | M
16111101006 | Cable Tray - 6 inch | M
16111201001 | Cable Tray Fittings - 36 inch | Ea
16111201002 | Cable Tray Fittings - 30 inch | Ea
16111201003 | Cable Tray Fittings - 24 inch | Ea
16111201004 | Cable Tray Fittings - 18 inch | Ea
16111201005 | Cable Tray Fittings - 12 inch | Ea
16111201006 | Cable Tray Fittings - 6 inch | Ea
16111401007 | Channel - 4 inch and below | M
16111501006 | Conduits - 6 inch | M
16111501007 | Conduits - 4 inch and below | M
16122102001 | MV Cable (15KV to 35KV) - 600 mcm and larger | M
16122102002 | MV Cable (15KV to 35KV) - 250 mcm to 500 mcm | M
16122102003 | MV Cable (15KV to 35KV) - AWG 1/0 to AWG 2 | M
16122202001 | MV Cable (2KV to 10KV) - 600 mcm and larger | M
16122202002 | MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | M
16122202003 | MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | M
16122202004 | MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | M
16122202005 | MV Cable (2KV to 10KV) - AWG14 and smaller | M
16122302001 | LV Cable (1KV/600V) - 600 mcm and larger | M
16122302002 | LV Cable (1KV/600V) - 250 mcm to 500 mcm | M
16122302003 | LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | M
16122302004 | LV Cable (1KV/600V) - AWG 12 to AWG 3 | M
16122302005 | LV Cable (1KV/600V) - AWG14 and smaller | M
16122402005 | Control/Instrument Cable - AWG14 and smaller | M
1612250 | Unused -
16122602003 | Grounding Wire - AWG 1/0 to AWG 2 | M
16122602004 | Grounding Wire - AWG 12 to AWG 3 | M
16122709999 | Fiberoptic Cable | M
16122809999 | Ethernet Cable | M
16132102001 | Connectors - MV Cable (15KV to 35KV) - 600 mcm and larger | Ea
16132102002 | Connectors - MV Cable (15KV to 35KV) - 250 mcm to 500 mcm | Ea
16132102003 | Connectors - MV Cable (15KV to 35KV) - AWG 1/0 to AWG 2 | Ea
16132202001 | Connectors - MV Cable (2KV to 10KV) - 600 mcm and larger | Ea
16132202002 | Connectors - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Ea
16132202003 | Connectors - MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | Ea
16132202004 | Connectors - MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | Ea
16132202005 | Connectors - MV Cable (2KV to 10KV) - AWG14 and smaller | Ea
16132302001 | Connectors - LV Cable (1KV/600V) - 600 mcm and larger | Ea
16132302002 | Connectors - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Ea
16132302003 | Connectors - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Ea
16132302004 | Connectors - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Ea
16132302005 | Connectors - LV Cable (1KV/600V) - AWG14 and smaller | Ea
16132402005 | Connectors - Control/Instrument Cable - AWG14 and smaller | Ea
16132709999 | Connectors - Fiberoptic Cable - Not Applicable | Ea
16132809999 | Connectors - Ethernet Cable - Not Applicable | Ea
16142102001 | Terminations - MV Cable (15KV to 35KV) - 600 mcm and larger | Ea
16142102002 | Terminations - MV Cable (15KV to 35KV) - 250 mcm to 500 mcm | Ea
16142102003 | Terminations - MV Cable (15KV to 35KV) - AWG 1/0 to AWG 2 | Ea
16142202001 | Terminations - MV Cable (2KV to 10KV) - 600 mcm and larger | Ea
16142202002 | Terminations - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Ea
16142202003 | Terminations - MV Cable (2KV to 10KV) - AWG 1/0 to AWG 2 | Ea
16142202004 | Terminations - MV Cable (2KV to 10KV) - AWG 12 to AWG 3 | Ea
16142202005 | Terminations - MV Cable (2KV to 10KV) - AWG14 and smaller | Ea
16142302001 | Terminations - LV Cable (1KV/600V) - 600 mcm and larger | Ea
16142302002 | Terminations - LV Cable (1KV/600V) - 250 mcm to 500 mcm | Ea
16142302003 | Terminations - LV Cable (1KV/600V) - AWG 1/0 to AWG 2 | Ea
16142302004 | Terminations - LV Cable (1KV/600V) - AWG 12 to AWG 3 | Ea
16142302005 | Terminations - LV Cable (1KV/600V) - AWG14 and smaller | Ea
16142402005 | Terminations - Control/Instrument Cable - AWG14 and smaller | Ea
1614250 | Terminations - Unused -
16142602003 | Terminations - Grounding Wire - AWG 1/0 to AWG 2 | Ea
16142602004 | Terminations - Grounding Wire - AWG 12 to AWG 3 | Ea
16142709999 | Terminations - Fiberoptic Cable - Not Applicable | Ea
16142809999 | Terminations - Ethernet Cable - Not Applicable | Ea
16152102001 | Splices - MV Cable (15KV to 35KV) - 600 mcm and larger | Ea
16152102002 | Splices - MV Cable (15KV to 35KV) - 250 mcm to 500 mcm | Ea
16152102003 | Splices - MV Cable (15KV to 35KV) - AWG 1/0 to AWG 2 | Ea
16152202001 | Splices - MV Cable (2KV to 10KV) - 600 mcm and larger | Ea
16152202002 | Splices - MV Cable (2KV to 10KV) - 250 mcm to 500 mcm | Ea
16199109109 | Allowance for Miscellaneous Items | Lot
Electrical Bulks Labor - Code of Accounts
Go to Tab Index